DIVISION 28 23 23

FVT10C1 SERIES – FIBER OPTIC TRANSMITTER

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- Fiber Optic Digital Video and Contact Closure Receiver

1.02 SECTION INCLUDES

- FVT10C1(M,S)1[/M] Series 10-Bit Digital Video and Contact Closure– Compact, Standalone and Rack Mount

1.03 REFERENCES

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide a digital Video Transmitter and integrated contact closure transmission system that transmits one (1) one-way video and one (1) contact closure.

- The system shall utilize optics operating at 1310nm capable of simultaneous video and contact closure transmission on one multimode optical fiber. (FVT10C1M1[/M])

- The system shall utilize optics operating at 1310nm capable of simultaneous video and contact closure transmission on one singlemode optical fiber. (FVT10C1S1[/M])

1.05 SUBMITTALS

- Product Data: Manufacturer’s printed product data sheet for each type of Receiver specified.

- Detail Drawings: Electrical and optical connect drawings. Product mounting template.

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of Receiver specified.

- Test Reports: Manufacturer’s Printed Test Report via a Tektronics VM700A Video Test Generator verifying product performance meets or exceeds the specified product performance referenced in Part 2.

- Warranty: Manufacturer’s Printed Warranty

1.06 DELIVERY, STORAGE AND HANDLING

- Deliver materials in unopened factory packaging with Manufacturer’s bar coding to the job site.

- Inspect product upon delivery to assure that specified products have been received.

- Store in original packaging in a climate controlled environment. Storage Temperature not to exceed: -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing). If product is installed in condensation conditions, unit shall have conformal coating applied to the printed circuit board.

1.08 WARRANTY

- Standard Communication Networks Comprehensive Lifetime Warranty: ComNet warrants the product to be free of factory defects under manufacture’s Lifetime Warranty as submitted under article 1.05 (E)

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer: Communication Networks, Inc.; 3 Corporate Drive, Danbury, CT 06810 USA; Telephone: 203-796-5300; Fax 203-796-5303; Email: sales@ComNet.net  Internet: www.ComNet.net

- Substitutions: Not Permitted

- All fiber optic modules shall be supplied from a single manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

2.03 GENERAL SPECIFICATIONS

- The digital video and contact closure transmitter shall be a ComNet FVT10C1(M,S)1[/M] series module. The module shall be capable of transmitting one (1) full color video in real time in NTSC, PAL or SECAM formats and one (1) contact closure. The module shall require no in-field electrical or optical adjustments or in-line attenuators to ease installation. The module shall provide video input, link and contact closure status indicating LED’s for monitoring proper system operation. The modules shall provide automatic re-settable solid-state current limiters and independent voltage regulators on each module to reduce the chance of a single point failure of the system. The module shall have an MTBF of >100,000 hours and operate in an environment of –40˚ C to +75˚ C and relative humidity between 0% to 95% (non-condensing). The module shall be UL and ULC listed and CE marked. The circuit board shall be UL 94 flame rated and meet all PCI standards. All PC boards shall be designated with part number, PC board number and show appropriate revision number. Housing shall be of anodized aluminium construction. All LED indicators and both electrical and mechanical connections shall be identified with silk-screened labels. The module shall have a lifetime warranty to reduce system life cycle cost in an event of a module failure.

2.04 VIDEO SPECIFICATIONS

- Input Video: 1 volt pk-pk (75 ohms)

- Bandwidth: 5 Hz – 10MHz

- Differential Gain: < 2 %.

- Differential Phase: < 0.7 °

- Tilt: 1%

- Signal/Noise Ratio: > 60dB @ max attenuation

2.05 CONTACT CLOSURE SPECIFICATIONS

- Dry Contact Closure (0.5A Contact Rating – normally open)

- Interface: Response Time: 0.5 msec

2.06 OPTICAL SPECIFICATIONS

- ComNet Model Number FVT10C1M1[/M] Optical Fiber: 50/125 or 62.5/125 micron multimode

- Number of Fibers Required: 1

- Optical Wavelength: 1310nm

- Optical Emitter Type: Laser Diode

- Optical Power Budget: 12 dB

- Optical Attenuation: No manual adjustments required

- ComNet Model Number FVT10C1S1[/M]

- Optical Fiber: 9/125 micron single mode

- Number of Fibers Required: 1

- Optical Wavelength: 1310nm

- Optical Emitter Type: Laser Diode

- Optical Power Budget: 16 dB

- Optical Attenuation: No manual adjustments required

2.07 STATUS INDICATORS

- Link: Link Active/Green – No Link/Red

- Video: Video Present/Green – No Video/Red

- Contact Closure: Contact Input Open/Off – Contact Input Closed/Green

2.08 CONNECTORS

- Optical: ST

- Power and Contact Closure: Terminal Block with Screw Clamps

- Video: BNC (Gold Plated Center-PIN)

2.09 ELECTRICAL SPECIFICATIONS

- Power

- Voltage Range: 9-36VDC or 12-24VAC Compact Size, 8-15 VDC Standalone/Rack Size

- Power Consumption: 2W

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

- Circuit Board: UL 94 flame rated and meets all PCI standards.

2.10 MECHANICAL SPECIFICATIONS

- Compact Mount Dimensions: 4.5” x 2.2” x 1.1” (11.7 cm x 5.5 cm x 2.8 cm)

- Standalone/Rack Mount Dimensions: 6.1” x 5.3” x 1.1” (15.5 cm x 13.5 cm x 2.8 cm)

- Number of Rack Slots: 1

- Finish: Module shall be constructed of a anodized aluminium with all connections and indicators silk-screened directly on unit.

- Weight: <2 lb./0.9 kg.

- This product shall conform to ComFit Technology.  That is, all “stand alone” products (sometimes called “box”) shall be identical in every respect, both electrically and physically,

with the “rack”  products so that only a single product may be used interchangeably for both the “stand alone” and “rack” applications.  All ComFit products shall be supplied with a plug-in module power supply, electrical connectors, and mechanical parts to enable it to be used in “stand alone” or “rack” configuration.  All ComFit products shall mount directly to a wall without the need for special mounting brackets.

2.11 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C

- Storage Temp: -40˚ C to +85˚ C

- Relative Humidity: 0% to 95% (non-condensing). If product is installed under condensation conditions, unit shall have conformal coating applied to the printed circuit board. (Add /C to model number for conformal coated printed circuit board)

2.12 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Underwriters Laboratory (UL) Listing Number: I.T.E. 6D16

- Underwriters Laboratory Canada (ULC) Listing Number: I.T.E. 6D16

- UL 94-flame rated PCB board: 94VO

2.13 ACCESSORIES

PART 3 - EXECUTION

3.01 EXAMINATION

- Inspect modules before installation.

- Modules shall be free of any cosmetic defects or damage.

- All optical connectors shall be covered with dust caps and remain on the module until installing cable connectors to module.

- Shipping box shall include the module, power supply and operations manual.

3.02 PREPARATION

- Standalone/Compact Modules (Surface Mount)

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet mounting template and installation manual.

- Rack Mount Module (19” Rack)

- Shall be installed in the ComNet Model Number C1/C2/C3 card cage. Ensure the card cage is installed in a standard EIA 19” (482.6 mm) rack or wall standoff bracket adequate for the size and weight of the card cage. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet installation manual.

- Optical Fibers

- Caution: NEVER look into the end of an active optical fiber when using laser light output. Eye damage can occur. Wear eye protection when cleaving, terminating, and splicing fiber.

- The number and type (multimode or single-mode) of optical fiber shall meet the requirements of the ComNet model number in article 2.06 used in the installation.

- All optical fiber cables shall be properly installed and terminated with the mating optical connectors as submitted in article 2.08 (A).

- The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3dB of optical safety margin does not exceed the optical power budget as submitted in article 2.06.

- All optical connectors on cable shall be cleaned in compliance to optical connector manufactures specifications and covered with dust caps until connection to the fiber optic module.

3.03 INSTALLATION

- General: Locate fiber optic modules as indicated on the approved detail drawings and install module in compliance with the ComNet installation and operations manual.

3.04 TESTING

- Testing the Fiber Optic Video Link.

- Verify that the coax and optic fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, camera, and video monitor or other equipment used in the system.

- Successful video link operation should be visible at this point as witnessed by a good quality video picture on the monitor.

- Testing the Fiber Optic Contact Closure Link.

- Verify that the contact leads and optical fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, controllers, and receiver drivers or other equipment used in the system.

- Close the contact on the transmitter unit and the corresponding contact should close on the receiver unit as indicated by the LED.

3.05 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all fiber scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| FVT10C1 SERIES | DESCRIPTION |
| --- | --- |
| FVT10C1M1 | Video & Contact Closure Receiver, Multimode, 1 Fiber |
| FVT10C1M1/M | Video & Contact Closure Receiver, Multimode, 1 Fiber, Mini Size |
| FVT10C1S1 FVT10C1S1/M | Video & Contact Closure Receiver, Singlemode, 1 Fiber Video & Contact Closure Receiver, Singlemode, 1 Fiber, Mini Size |

Table B: Product Compatibility Chart

| TRANSMITTER | COMPATIBLE RECEIVER |
| --- | --- |
| FVT10C1M1/M, FVT10C1M1 | FVR10C1M1, FVR20C2M2, FVR40C4M4 |
| FVT10C1S1/M, FVT10C1S1 | FVR10C1S1, FVR20C2S2, FVR40C4S4 |

## END OF SECTION

DIVISION 28 23 23

FVR10C1 SERIES – FIBER OPTIC RECEIVER

ENGINEERING SPECIFICATIONS

- PART 1 - GENERAL

1.01 SUMMARY

- Fiber Optic Digital Video and Contact Closure Receiver

1.02 SECTION INCLUDES

- FVR10C1(M,S)1 Series Digital Video and Contact Closure– Standalone and Rack Mount

1.03 REFERENCES

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide a digital Video Receiver and integrated contact closure receiver system that receives one (1) one-way video and one (1) contact closure.

- The system shall utilize optics operating at 1310nm capable of simultaneous video and contact closure reception on one multimode optical fiber. (FVR10C1M1)

- The system shall utilize optics operating at 1310nm capable of simultaneous video and contact closure reception on one singlemode optical fiber. (FVR10C1S1)

1.05 SUBMITTALS

- Product Data: Manufacturer’s printed product data sheet for each type of Receiver specified.

- Detail Drawings: Electrical and optical connect drawings. Product mounting template.

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of Receiver specified.

- Test Reports: Manufacturer’s Printed Test Report via a Tektronics VM700A Video Test Generator verifying product performance meets or exceeds the specified product performance referenced in Part 2.

- Warranty: Manufacturer’s Printed Warranty

1.06 DELIVERY, STORAGE AND HANDLING

- Deliver materials in unopened factory packaging with Manufacturer’s bar coding to the job site.

- Inspect product upon delivery to assure that specified products have been received.

- Store in original packaging in a climate controlled environment. Storage Temperature not to exceed: -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing). If product is installed in condensation conditions, unit shall have conformal coating applied to the printed circuit board.

1.08 WARRANTY

- Standard Communication Networks Comprehensive Lifetime Warranty: ComNet warrants the product to be free of factory defects under manufacture’s Lifetime Warranty as submitted under article 1.05 (E)

- PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer: Communication Networks, Inc.; 3 Corporate Drive, Danbury, CT 06810 USA; Telephone: 203-796-5300; Fax 203-796-5303; Email: sales@ComNet.net  Internet: www.ComNet.net

- Substitutions: Not Permitted

- All fiber optic modules shall be supplied from a single manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

2.03 GENERAL SPECIFICATIONS

- The digital video and contact closure receiver system shall be a ComNet FVR10C1(M,S)1 series module. The module shall be capable of receiving one (1) full color video in real time in NTSC, PAL or SECAM formats and one (1) contact closure. The module shall require no in-field electrical or optical adjustments or in-line attenuators to ease installation. The module shall provide video input, link and contact closure status indicating LED’s for monitoring proper system operation. The modules shall provide automatic re-settable solid-state current limiters and independent voltage regulators on each module to reduce the chance of a single point failure of the system. The module shall have an MTBF of >100,000 hours and operate in an environment of –40˚ C to +75˚ C and relative humidity between 0% to 95% (non-condensing). The module shall be UL and ULC listed and CE marked. The circuit board shall be UL 94 flame rated and meet all PCI standards. All PC boards shall be designated with part number, PC board number and show appropriate revision number. Housing shall be of anodized aluminium construction. All LED indicators and both electrical and mechanical connections shall be identified with silk-screened labels. The module shall have a lifetime warranty to reduce system life cycle cost in an event of a module failure.

2.04 VIDEO SPECIFICATIONS

- Input Video: 1 volt pk-pk (75 ohms)

- Bandwidth: 5 Hz – 10MHz

- Differential Gain: < 2 %.

- Differential Phase: < 0.7 °

- Tilt: 1%

- Signal/Noise Ratio: > 60dB @ max attenuation

2.05 CONTACT CLOSURE SPECIFICATIONS

- Dry Contact Closure (0.5A Contact Rating – normally open)

- Interface: Response Time: 0.5 msec

2.06 OPTICAL SPECIFICATIONS

- ComNet Model Number FVR10C1M1 Optical Fiber: 50/125 or 62.5/125 micron multimode

- Number of Fibers Required: 1

- Optical Wavelength: 1310nm

- Optical Detector Type: Pin Diode

- Optical Power Budget: 12 dB

- Optical Attenuation: No manual adjustments required

- ComNet Model Number FVR10C1S1

- Optical Fiber: 9/125 micron single mode

- Number of Fibers Required: 1

- Optical Wavelength: 1310nm

- Optical Detector Type: Pin Diode

- Optical Power Budget: 16 dB

- Optical Attenuation: No manual adjustments required

2.07 STATUS INDICATORS

- Link: Link Active/Green – No Link/Red

- Video: Video Present/Green – No Video/Red

- Contact Closure: Contact Input Open/Off – Contact Input Closed/Green

2.08 CONNECTORS

- Optical: ST

- Power and Contact Closure: Terminal Block with Screw Clamps

- Video: BNC (Gold Plated Center-PIN)

2.09 ELECTRICAL SPECIFICATIONS

- Power

- Voltage Range: 8-15 VDC

- Power Consumption: 2W

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

- Circuit Board: UL 94 flame rated and meets all PCI standards.

2.10 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions – Standard Size: 6.1” x 5.3” x 1.1” (15.5 cm x 13.5 cm x 2.8 cm)

- Rack Mount Dimensions: 6.1” x 5.3” x 1.1” (15.5 cm x 13.5 cm x 2.8 cm)

- Number of Rack Slots: 1

- Finish: Module shall be constructed of a anodized aluminium with all connections and indicators silk-screened directly on unit.

- Weight: <2 lb./0.9 kg.

- This product shall conform to ComFit Technology.  That is, all “stand alone” products (sometimes called “box”) shall be identical in every respect, both electrically and physically,

with the “rack”  products so that only a single product may be used interchangeably for both the “stand alone” and “rack” applications.  All ComFit products shall be supplied with a plug-in module power supply, electrical connectors, and mechanical parts to enable it to be used in “stand alone” or “rack” configuration.  All ComFit products shall mount directly to a wall without the need for special mounting brackets.

2.11 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C

- Storage Temp: -40˚ C to +85˚ C

- Relative Humidity: 0% to 95% (non-condensing). If product is installed under condensation conditions, unit shall have conformal coating applied to the printed circuit board. (Add /C to model number for conformal coated printed circuit board)

2.12 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Underwriters Laboratory (UL) Listing Number: I.T.E. 6D16

- Underwriters Laboratory Canada (ULC) Listing Number: I.T.E. 6D16

- UL 94-flame rated PCB board: 94VO

2.13 ACCESSORIES

PART 3 - EXECUTION

3.01 EXAMINATION

- Inspect modules before installation.

- Modules shall be free of any cosmetic defects or damage.

- All optical connectors shall be covered with dust caps and remain on the module until installing cable connectors to module.

- Shipping box shall include the module, power supply and operations manual.

3.02 PREPARATION

- Standalone Module (Surface Mount)

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet mounting template and installation manual.

- Rack Mount Module (19” Rack)

- Shall be installed in the ComNet Model Number C1/C2/C3 card cage. Ensure the card cage is installed in a standard EIA 19” (482.6 mm) rack or wall standoff bracket adequate for the size and weight of the card cage. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet installation manual.

- Optical Fibers

- Caution: NEVER look into the end of an active optical fiber when using laser light output. Eye damage can occur. Wear eye protection when cleaving, terminating, and splicing fiber.

- The number and type (multimode or single-mode) of optical fiber shall meet the requirements of the ComNet model number in article 2.06 used in the installation.

- All optical fiber cables shall be properly installed and terminated with the mating optical connectors as submitted in article 2.08 (A).

- The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3dB of optical safety margin does not exceed the optical power budget as submitted in article 2.06.

- All optical connectors on cable shall be cleaned in compliance to optical connector manufactures specifications and covered with dust caps until connection to the fiber optic module.

3.03 INSTALLATION

- General: Locate fiber optic modules as indicated on the approved detail drawings and install module in compliance with the ComNet installation and operations manual.

3.04 TESTING

- Testing the Fiber Optic Video Link.

- Verify that the coax and optic fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, camera, and video monitor or other equipment used in the system.

- Successful video link operation should be visible at this point as witnessed by a good quality video picture on the monitor.

- Testing the Fiber Optic Contact Closure Link.

- Verify that the contact leads and optical fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, controllers, and receiver drivers or other equipment used in the system.

- Close the contact on the transmitter unit and the corresponding contact should close on the receiver unit as indicated by the LED.

3.05 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all fiber scraps properly.

- MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| FVR10C1 SERIES | DESCRIPTION |
| --- | --- |
| FVR10C1M1 | Video & Contact Closure Receiver, Multimode, 1 Fiber |
| FVR10C1S1 | Video & Contact Closure Receiver, Singlemode, 1 Fiber |

Table B: Product Compatibility Chart

| TRANSMITTER | COMPATIBLE RECEIVER |
| --- | --- |
| FVT1M1/M, FVT10C1M1/M, FVT10C1M1 | FVR10C1M1 |
| FVT1S1/M, FVT10C1S1/M, FVT10C1S1 | FVR10C1S1 |

- END OF SECTION

DIVISION 28 23 23

FVR20C2 SERIES – FIBER OPTIC RECEIVER

ENGINEERING SPECIFICATIONS

- PART 1 - GENERAL

1.01 SUMMARY

- Fiber Optic Digital Video and Contact Closure Receiver

1.02 SECTION INCLUDES

- FVR20C2(M,S)2 Series Digital Video and Contact Closure– Standalone and Rack Mount

1.03 REFERENCES

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide a digital Video Receiver and integrated contact closure receiver system that receives two (2) one-way video and two (2) contact closures.

- The system shall utilize optics operating at 1310nm capable of simultaneous video and contact closure reception on two multimode optical fibers. (FVR20C2M2)

- The system shall utilize optics operating at 1310nm capable of simultaneous video and contact closure reception on two singlemode optical fibers. (FVR20C2S2)

1.05 SUBMITTALS

- Product Data: Manufacturer’s printed product data sheet for each type of Receiver specified.

- Detail Drawings: Electrical and optical connect drawings. Product mounting template.

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of Receiver specified.

- Test Reports: Manufacturer’s Printed Test Report via a Tektronics VM700A Video Test Generator verifying product performance meets or exceeds the specified product performance referenced in Part 2.

- Warranty: Manufacturer’s Printed Warranty

1.06 DELIVERY, STORAGE AND HANDLING

- Deliver materials in unopened factory packaging with Manufacturer’s bar coding to the job site.

- Inspect product upon delivery to assure that specified products have been received.

- Store in original packaging in a climate controlled environment. Storage Temperature not to exceed: -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing). If product is installed in condensation conditions, unit shall have conformal coating applied to the printed circuit board.

1.08 WARRANTY

- Standard Communication Networks Comprehensive Lifetime Warranty: ComNet warrants the product to be free of factory defects under manufacture’s Lifetime Warranty as submitted under article 1.05 (E)

- PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer: Communication Networks, Inc.; 3 Corporate Drive, Danbury, CT 06810 USA; Telephone: 203-796-5300; Fax 203-796-5303; Email: sales@ComNet.net  Internet: www.ComNet.net

- Substitutions: Not Permitted

- All fiber optic modules shall be supplied from a single manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

2.03 GENERAL SPECIFICATIONS

- The digital video and contact closure receiver system shall be a ComNet FVR20C2(M,S)2 series module. The module shall be capable of receiving two (2) full color video in real time in NTSC, PAL or SECAM formats and two (2) contact closures. Two individual receiving units each with individual optical receiver shall be housed in the module. The module shall require no in-field electrical or optical adjustments or in-line attenuators to ease installation. The module shall provide video input, link and contact closure status indicating LED’s for monitoring proper system operation. The modules shall provide automatic re-settable solid-state current limiters and independent voltage regulators on each module to reduce the chance of a single point failure of the system. The module shall have an MTBF of >100,000 hours and operate in an environment of –40˚ C to +75˚ C and relative humidity between 0% to 95% (non-condensing). The module shall be UL and ULC listed and CE marked. The circuit board shall be UL 94 flame rated and meet all PCI standards. All PC boards shall be designated with part number, PC board number and show appropriate revision number. Housing shall be of anodized aluminium construction. All LED indicators and both electrical and mechanical connections shall be identified with silk-screened labels. The module shall have a lifetime warranty to reduce system life cycle cost in an event of a module failure.

2.04 VIDEO SPECIFICATIONS

- Input Video: 1 volt pk-pk (75 ohms)

- Bandwidth: 5 Hz – 10MHz

- Differential Gain: < 2 %.

- Differential Phase: < 0.7 °

- Tilt: 1%

- Signal/Noise Ratio: > 60dB @ max attenuation

2.05 CONTACT CLOSURE SPECIFICATIONS

- Dry Contact Closure (0.5A Contact Rating – normally open)

- Interface: Response Time: 0.5 msec

2.06 OPTICAL SPECIFICATIONS

- ComNet Model Number FVR20C2M2 Optical Fiber: 50/125 or 62.5/125 micron multimode

- Number of Fibers Required: 2

- Optical Wavelength: 1310nm

- Optical Detector Type: Pin Diode

- Optical Power Budget: 12 dB

- Optical Attenuation: No manual adjustments required

- ComNet Model Number FVR20C2S2

- Optical Fiber: 9/125 micron single mode

- Number of Fibers Required: 2

- Optical Wavelength: 1310nm

- Optical Detector Type: Pin Diode

- Optical Power Budget: 16 dB

- Optical Attenuation: No manual adjustments required

2.07 STATUS INDICATORS

- Link: Link Active/Green – No Link/Red

- Video: Video Present/Green – No Video/Red

- Contact Closure: Contact Input Open/Off – Contact Input Closed/Green

2.08 CONNECTORS

- Optical: ST

- Power and Contact Closure: Terminal Block with Screw Clamps

- Video: BNC (Gold Plated Center-PIN)

2.09 ELECTRICAL SPECIFICATIONS

- Power

- Voltage Range: 8-15 VDC

- Power Consumption: 2W

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

- Circuit Board: UL 94 flame rated and meets all PCI standards.

2.10 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions – Standard Size: 6.1” x 5.3” x 1.1” (15.5 cm x 13.5 cm x 2.8 cm)

- Rack Mount Dimensions: 6.1” x 5.3” x 1.1” (15.5 cm x 13.5 cm x 2.8 cm)

- Number of Rack Slots: 1

- Finish: Module shall be constructed of a anodized aluminium with all connections and indicators silk-screened directly on unit.

- Weight: <2 lb./0.9 kg.

- This product shall conform to ComFit Technology.  That is, all “stand alone” products (sometimes called “box”) shall be identical in every respect, both electrically and physically,

with the “rack”  products so that only a single product may be used interchangeably for both the “stand alone” and “rack” applications.  All ComFit products shall be supplied with a plug-in module power supply, electrical connectors, and mechanical parts to enable it to be used in “stand alone” or “rack” configuration.  All ComFit products shall mount directly to a wall without the need for special mounting brackets.

2.11 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C

- Storage Temp: -40˚ C to +85˚ C

- Relative Humidity: 0% to 95% (non-condensing). If product is installed under condensation conditions, unit shall have conformal coating applied to the printed circuit board. (Add /C to model number for conformal coated printed circuit board)

2.12 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Underwriters Laboratory (UL) Listing Number: I.T.E. 6D16

- Underwriters Laboratory Canada (ULC) Listing Number: I.T.E. 6D16

- UL 94-flame rated PCB board: 94VO

2.13 ACCESSORIES

PART 3 - EXECUTION

3.01 EXAMINATION

- Inspect modules before installation.

- Modules shall be free of any cosmetic defects or damage.

- All optical connectors shall be covered with dust caps and remain on the module until installing cable connectors to module.

- Shipping box shall include the module, power supply and operations manual.

3.02 PREPARATION

- Standalone Module (Surface Mount)

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet mounting template and installation manual.

- Rack Mount Module (19” Rack)

- Shall be installed in the ComNet Model Number C1/C2/C3 card cage. Ensure the card cage is installed in a standard EIA 19” (482.6 mm) rack or wall standoff bracket adequate for the size and weight of the card cage. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet installation manual.

- Optical Fibers

- Caution: NEVER look into the end of an active optical fiber when using laser light output. Eye damage can occur. Wear eye protection when cleaving, terminating, and splicing fiber.

- The number and type (multimode or single-mode) of optical fiber shall meet the requirements of the ComNet model number in article 2.06 used in the installation.

- All optical fiber cables shall be properly installed and terminated with the mating optical connectors as submitted in article 2.08 (A).

- The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3dB of optical safety margin does not exceed the optical power budget as submitted in article 2.06.

- All optical connectors on cable shall be cleaned in compliance to optical connector manufactures specifications and covered with dust caps until connection to the fiber optic module.

3.03 INSTALLATION

- General: Locate fiber optic modules as indicated on the approved detail drawings and install module in compliance with the ComNet installation and operations manual.

3.04 TESTING

- Testing the Fiber Optic Video Link.

- Verify that the coax and optic fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, camera, and video monitor or other equipment used in the system.

- Successful video link operation should be visible at this point as witnessed by a good quality video picture on the monitor.

- Testing the Fiber Optic Contact Closure Link.

- Verify that the contact leads and optical fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, controllers, and receiver drivers or other equipment used in the system.

- Close the contact on the transmitter unit and the corresponding contact should close on the receiver unit as indicated by the LED.

3.05 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all fiber scraps properly.

- MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| FVR20C2 SERIES | DESCRIPTION |
| --- | --- |
| FVR20C2M2 | 2 Channel Video & Contact Closure Receiver, Multimode, 2 Fibers |
| FVR20C2S2 | 2 Channel Video & Contact Closure Receiver, Singlemode, 2 Fibers |

Table B: Product Compatibility Chart

| TRANSMITTER | COMPATIBLE RECEIVER |
| --- | --- |
| FVT1M1/M, FVT10C1M1/M, FVT10C1M1 | FVR20C2M2 |
| FVT1S1/M, FVT10C1S1/M, FVT10C1S1 | FVR20C2S2 |

- END OF SECTION

DIVISION 28 23 23

FVR40C4 SERIES – FIBER OPTIC RECEIVER

ENGINEERING SPECIFICATIONS

- PART 1 - GENERAL

1.01 SUMMARY

- Fiber Optic Digital Video and Contact Closure Receiver

1.02 SECTION INCLUDES

- FVR40C4(M,S)4 Series Digital Video and Contact Closure– Standalone and Rack Mount

1.03 REFERENCES

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide a digital Video Receiver and integrated contact closure receiver system that receives four (4) one-way video and four (4) contact closures.

- The system shall utilize optics operating at 1310nm capable of simultaneous video and contact closure reception on four multimode optical fibers. (FVR40C4M4)

- The system shall utilize optics operating at 1310nm capable of simultaneous video and contact closure reception on four singlemode optical fibers. (FVR40C4S4)

1.05 SUBMITTALS

- Product Data: Manufacturer’s printed product data sheet for each type of Receiver specified.

- Detail Drawings: Electrical and optical connect drawings. Product mounting template.

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of Receiver specified.

- Test Reports: Manufacturer’s Printed Test Report via a Tektronics VM700A Video Test Generator verifying product performance meets or exceeds the specified product performance referenced in Part 2.

- Warranty: Manufacturer’s Printed Warranty

1.06 DELIVERY, STORAGE AND HANDLING

- Deliver materials in unopened factory packaging with Manufacturer’s bar coding to the job site.

- Inspect product upon delivery to assure that specified products have been received.

- Store in original packaging in a climate controlled environment. Storage Temperature not to exceed: -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing). If product is installed in condensation conditions, unit shall have conformal coating applied to the printed circuit board.

1.08 WARRANTY

- Standard Communication Networks Comprehensive Lifetime Warranty: ComNet warrants the product to be free of factory defects under manufacture’s Lifetime Warranty as submitted under article 1.05 (E)

- PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer: Communication Networks, Inc.; 3 Corporate Drive, Danbury, CT 06810 USA; Telephone: 203-796-5300; Fax 203-796-5303; Email: sales@ComNet.net  Internet: www.ComNet.net

- Substitutions: Not Permitted

- All fiber optic modules shall be supplied from a single manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

2.03 GENERAL SPECIFICATIONS

- The digital video and contact closure receiver system shall be a ComNet FVR40C4(M,S)4 series module. The module shall be capable of receiving four (4) full color video in real time in NTSC, PAL or SECAM formats and four (4) contact closures. Four individual receiving units each with individual optical receiver shall be housed in the module. The module shall require no in-field electrical or optical adjustments or in-line attenuators to ease installation. The module shall provide video input, link and contact closure status indicating LED’s for monitoring proper system operation. The modules shall provide automatic re-settable solid-state current limiters and independent voltage regulators on each module to reduce the chance of a single point failure of the system. The module shall have an MTBF of >100,000 hours and operate in an environment of –40˚ C to +75˚ C and relative humidity between 0% to 95% (non-condensing). The module shall be UL and ULC listed and CE marked. The circuit board shall be UL 94 flame rated and meet all PCI standards. All PC boards shall be designated with part number, PC board number and show appropriate revision number. Housing shall be of anodized aluminium construction. All LED indicators and both electrical and mechanical connections shall be identified with silk-screened labels. The module shall have a lifetime warranty to reduce system life cycle cost in an event of a module failure.

2.04 VIDEO SPECIFICATIONS

- Input Video: 1 volt pk-pk (75 ohms)

- Bandwidth: 5 Hz – 10MHz

- Differential Gain: < 2 %.

- Differential Phase: < 0.7 °

- Tilt: 1%

- Signal/Noise Ratio: > 60dB @ max attenuation

2.05 CONTACT CLOSURE SPECIFICATIONS

- Dry Contact Closure (0.5A Contact Rating – normally open)

- Interface: Response Time: 0.5 msec

2.06 OPTICAL SPECIFICATIONS

- ComNet Model Number FVR40C4M4

- Optical Fiber: 50/125 or 62.5/125 micron multimode

- Number of Fibers Required: 4

- Optical Wavelength: 1310nm

- Optical Detector Type: Pin Diode

- Optical Power Budget: 12 dB

- Optical Attenuation: No manual adjustments required

- ComNet Model Number FVR40C4S4

- Optical Fiber: 9/125 micron single mode

- Number of Fibers Required: 4

- Optical Wavelength: 1310nm

- Optical Detector Type: Pin Diode

- Optical Power Budget: 16 dB

- Optical Attenuation: No manual adjustments required

2.07 STATUS INDICATORS

- Link: Link Active/Green – No Link/Red

- Video: Video Present/Green – No Video/Red

- Contact Closure: Contact Input Open/Off – Contact Input Closed/Green

2.08 CONNECTORS

- Optical: ST

- Power and Contact Closure: Terminal Block with Screw Clamps

- Video: BNC (Gold Plated Center-PIN)

2.09 ELECTRICAL SPECIFICATIONS

- Power

- Voltage Range: 8-15 VDC

- Power Consumption: 4W

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

- Circuit Board: UL 94 flame rated and meets all PCI standards.

2.10 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions – Standard Size: 6.1” x 5.3” x 1.1” (15.5 cm x 13.5 cm x 2.8 cm)

- Rack Mount Dimensions: 6.1” x 5.3” x 1.1” (15.5 cm x 13.5 cm x 2.8 cm)

- Number of Rack Slots: 1

- Finish: Module shall be constructed of a anodized aluminium with all connections and indicators silk-screened directly on unit.

- Weight: <2 lb./0.9 kg.

- This product shall conform to ComFit Technology.  That is, all “stand alone” products (sometimes called “box”) shall be identical in every respect, both electrically and physically,

with the “rack”  products so that only a single product may be used interchangeably for both the “stand alone” and “rack” applications.  All ComFit products shall be supplied with a plug-in module power supply, electrical connectors, and mechanical parts to enable it to be used in “stand alone” or “rack” configuration.  All ComFit products shall mount directly to a wall without the need for special mounting brackets.

2.11 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C

- Storage Temp: -40˚ C to +85˚ C

- Relative Humidity: 0% to 95% (non-condensing). If product is installed under condensation conditions, unit shall have conformal coating applied to the printed circuit board. (Add /C to model number for conformal coated printed circuit board)

2.12 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Underwriters Laboratory (UL) Listing Number: I.T.E. 6D16

- Underwriters Laboratory Canada (ULC) Listing Number: I.T.E. 6D16

- UL 94-flame rated PCB board: 94VO

2.13 ACCESSORIES

PART 3 - EXECUTION

3.01 EXAMINATION

- Inspect modules before installation.

- Modules shall be free of any cosmetic defects or damage.

- All optical connectors shall be covered with dust caps and remain on the module until installing cable connectors to module.

- Shipping box shall include the module, power supply and operations manual.

3.02 PREPARATION

- Standalone Module (Surface Mount)

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet mounting template and installation manual.

- Rack Mount Module (19” Rack)

- Shall be installed in the ComNet Model Number C1/C2/C3 card cage. Ensure the card cage is installed in a standard EIA 19” (482.6 mm) rack or wall standoff bracket adequate for the size and weight of the card cage. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet installation manual.

- Optical Fibers

- Caution: NEVER look into the end of an active optical fiber when using laser light output. Eye damage can occur. Wear eye protection when cleaving, terminating, and splicing fiber.

- The number and type (multimode or single-mode) of optical fiber shall meet the requirements of the ComNet model number in article 2.06 used in the installation.

- All optical fiber cables shall be properly installed and terminated with the mating optical connectors as submitted in article 2.08 (A).

- The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3dB of optical safety margin does not exceed the optical power budget as submitted in article 2.06.

- All optical connectors on cable shall be cleaned in compliance to optical connector manufactures specifications and covered with dust caps until connection to the fiber optic module.

3.03 INSTALLATION

- General: Locate fiber optic modules as indicated on the approved detail drawings and install module in compliance with the ComNet installation and operations manual.

3.04 TESTING

- Testing the Fiber Optic Video Link.

- Verify that the coax and optic fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, camera, and video monitor or other equipment used in the system.

- Successful video link operation should be visible at this point as witnessed by a good quality video picture on the monitor.

- Testing the Fiber Optic Contact Closure Link.

- Verify that the contact leads and optical fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, controllers, and receiver drivers or other equipment used in the system.

- Close the contact on the transmitter unit and the corresponding contact should close on the receiver unit as indicated by the LED.

3.05 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all fiber scraps properly

- MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| FVR40C4 SERIES | DESCRIPTION |
| --- | --- |
| FVR40C4M4 | 4 Channel Video & Contact Closure Receiver, Multimode, 4 Fibers |
| FVR40C4S4 | 4 Channel Video & Contact Closure Receiver, Singlemode, 4 Fibers |

Table B: Product Compatibility Chart

| TRANSMITTER | COMPATIBLE RECEIVER |
| --- | --- |
| FVT1M1/M, FVT10C1M1/M, FVT10C1M1 | FVR40C4M4 |
| FVT1S1/M, FVT10C1S1/M, FVT10C1S1 | FVR40C4S4 |

- END OF SECTION