DIVISION 28 23 23

FVT/FVR120D8 SERIES – FIBER OPTIC TRANSMITTER AND RECEIVER

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- Fiber optic 10-bit digital 12 channel video/8 channel data multiplexing system.

1.02 SECTION INCLUDES

- FVT/FVR120D8M1 10-bit digital 12 channel video/8 channel data multiplexing system, multimode rackmount

- FVT/FVR120D8S1 10-bit digital 12 channel video/8 channel data multiplexing system, singlemode, rackmount

1.03 REFERENCES

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide a 10-bit digital 12 channel video/8 channel data multiplexing system.  The system shall utilize LASER optics capable of 10-bit digitally encoding and decoding 12 channels of video and 8 channels of bi-directional data on one multimode optical fiber. (FVT/FVR120D8M1)

- The system shall utilize LASER optics capable of 10-bit digitally encoding and decoding 12 channels of video and 8 channels of bi-directional data on one single mode optical fiber. (FVT/FVR120D8S1)

1.05 SUBMITTALS

- Product Data: Manufacturer’s printed product data sheet for each type of transmitter and receiver specified.

- Detail Drawings: Electrical and optical connect drawings, product mounting template.

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of transmitter and receiver specified.

- Test Reports: Manufacturer’s printed test report via a Tektronics VM700A Video Test Generator verifying product performance meets or exceeds the specified product performance referenced in Part 2.

- Warranty: Manufacturer’s printed warranty

1.06 DELIVERY, STORAGE AND HANDLING

- Deliver materials to the job site in unopened factory packaging with manufacturer’s bar coding.

- Inspect product upon delivery to assure that specified products have been received.

- Store in original packaging in a climate controlled environment.  Storage temperature not to exceed: -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing).  If product is installed in condensation conditions, unit shall have conformal coating applied to the printed circuit board.

1.08 WARRANTY

- Standard Communication Networks Comprehensive Lifetime Warranty: ComNet warrants the product to be free of factory defects under manufacture’s Lifetime Warranty as submitted under article 1.05 (E)

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer

Communication Networks

3 Corporate Drive

Danbury CT 06810

U.S.A.

Telephone: 203 796-5300

e-mail: sales@comnet.net;

Internet URL: http://www.comnet.net

- Substitutions: Not permitted

- All fiber optic modules shall be supplied from a single manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

2.03 GENERAL SPECIFICATIONS

- The 10-bit digital 12-channel video/8 channel data encoding and decoding system shall be a ComNet FVT/FVR120D8 series module.  The module shall be capable of 10-bit digitally encoding and decoding 12 channels of full motion, real-time, color video in NTSC, PAL or SECAM formats along with 8 channels of bi-directional multi-protocol data (RS-232, RS-422, 2-wire RS-485, and 4-wire RS-485).  The module shall require no in-field electrical or optical adjustments or in-line attenuators.  The module shall transmit the video using state – of – the – art 10-bit digital encoding and decoding of the optical signal.  The module shall provide indicator LED’s for power, video sync for each channel, transmitted data and received data for each channel, and optical link lock status for monitoring proper system operation.  The modules shall provide automatic re-settable solid-state current limiters and independent voltage regulators on each module to reduce the chance that a single point failure will disable the system.  The module shall be hot swappable in a rack mount system to reduce complete system shut down during maintenance or repair.  The module shall have an MTBF of >100,000 hours and operate in an environment of –40˚ C to +75˚ C and relative humidity of 0% to 95% (non-condensing).  The module shall be UL and ULC listed and CE marked.  The circuit board shall be UL 94 flame rated and meet all PCI standards. All PC boards shall be designated with part number, PC board number and show appropriate revision number.  Housing shall be of all metal construction. All LED indicators and both electrical and mechanical connections shall be identified with silk-screened labels.  The module shall have a lifetime warranty to reduce system life cycle cost in the event of a module failure.

2.04 SPECIFICATIONS

- Video

- Input Video: 1 volt pk-pk (75 ohms)

- Input/Output Channels: 12

- Bandwidth: 5 Hz – 6.5 MHz

- Differential Gain: < 2 %

- Differential Phase: < 0.7 °

- Tilt: <1%

- Signal/Noise Ratio: 67 dB @ maximum optical loss budget

- Data

- Data Formats: Asynchronous, simplex, half duplex, or full duplex RS-232, RS-422, 2-wire RS-485, 4-wire RS-485, Sensornet, Manchester, Bi-phase, Pelco P, Pelco D (transparent to encoding)

- Data Rate: DC to 250 kbps (NRZ)

2.05 OPTICAL SPECIFICATIONS

- ComNet Model Number FVT/FVR120D8M1

- Optical Fiber: 50/125 µm or 62.5/125 µm multimode

- Number of Fibers Required: 1

- Optical Wavelengths: 1510 nm / 1530 nm

- Optical Power Budget: 18 dB @ 1310 nm into a 62.5 µm fiber core

- Optical Attenuation: no manual adjustments required

- ComNet Model Number FVT/FVR120D8S1

- Optical Fiber: singlemode

- Number of Fibers Required: 1

- Optical Wavelengths: 1510 nm / 1530 nm

- Optical Power Budget: 18 dB @ 1310 nm into a singlemode fiber core

- Optical Attenuation: no manual adjustments required

  - STATUS INDICATORS

- Power, video sync for each video channel, data in and data out for each data channel, and optical carrier.

2.07 CONNECTORS

- Optical: ST

- Power : terminal block with screw clamps

- Video: BNC (gold plated center pin)

- Data: RJ-45 receptacles (breakout cables automatically supplied for each RJ-45 receptacle)

2.08 ELECTRICAL SPECIFICATIONS

- Power:  8-15 VDC

- Current Protection: automatic re-settable solid-state current limiters

- Voltage Regulation: solid-state, independent on each board

- Circuit Board: UL 94 flame rated and meets all PCI standards.

- Rack-Mount Card: shall be hot-swappable within ComNet Model Number C1 (EIA 19” card cage)

2.09 MECHANICAL SPECIFICATIONS

- Dimensions (including C1 card cage): 19.0” x 7.5” x 6.9” (483 cm x 191 cm x 175 cm)

- Number of Rack Slots: 6

- Weight (including card cage): <11 lb/5.0 kg

2.10 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C

- Storage Temp: -40˚ C to +85˚ C

- Relative Humidity: 0% to 95% (non-condensing).  If product is installed under condensation conditions, unit shall have conformal coating applied to the printed circuit board.  (Add –C to model number for conformally coated printed circuit board)

2.11 ACCESSORIES

- Card Cage (included): ComNet model number C1 (EIA 19” card cage) shall be available to house and power rack mount modules.

- Blank Panels: ComNet Model Number C1-BP shall be available to cover unused rack slots.

PART 3 - EXECUTION

3.01 EXAMINATION

- Inspect modules before installation.

- Modules shall be free of any cosmetic defects or damage.

- All optical connectors shall be covered with dust caps and remain on the module until installing cable connectors to module.

- Shipping box shall include the module, power supply and operations manual.

3.02 PREPARATION

- Rack Mount Module (19” Rack)

Shall be installed in the ComNet Model Number C1 card cage. Ensure the card cage is installed in a standard EIA 19” (482.6 mm) rack or wall standoff bracket adequate for the size and weight of the card cage. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet installation manual.

- Optical Fibers

- Caution: NEVER look into the end of an active optical fiber when using laser light output. Eye damage can occur. Wear eye protection when cleaving, terminating, and splicing fiber.

- The number and type (multimode or single-mode) of optical fibers shall meet the requirements of the ComNet model number in article 2.05 used in the installation.

- All optical fiber cables shall be properly installed and terminated with the mating optical connectors as submitted in article 2.07 (A).

- The optical link shall be tested with an optical power meter kit, or with an OTDR.  An end-to-end optical path loss in both directions shall be made at 1310 nm to ensure that the optical path loss plus an added 3 dB of optical safety margin does not exceed the optical power budget as submitted in article 2.05.

- All connectors on the optical fiber cable shall be cleaned in compliance to optical connector manufactures specifications and covered with dust caps until connection to the fiber optic module.

3.03 INSTALLATION

- General: Locate fiber optic modules as indicated on the approved detail drawings and install the module in compliance with the ComNet installation and operations manual.

3.04 TESTING

- Testing the Fiber Optic Video Link.

- Verify that the coaxial cables and optical fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, camera, and video monitor or other equipment used in the system.

- Successful video link operation should be visible at this point as witnessed by a good quality video picture on the monitor.

3.05 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all fiber scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| FVT120D8 SERIES | DESCRIPTION | OPTICAL POWER BUDGET | MAXIMUM DISTANCE |
| --- | --- | --- | --- |
| FVT120D8M1 FVR120D8M1 | multimode, 12-channel video transmitter/8 channel data transceiver multimode, 12-channel video receiver/8 channel data transceiver | 18 dB @ 1310 nm into a 62.5 µm core | 0.6 miles (1 km) |
| FVT120D8S1 FVR120D8S1 | singlemode, 12-channel video transmitter/8 channel data transceiver singlemode, 12-channel video receiver/8 channel data transceiver | 18 dB @ 1310 nm into a singlemode core | 54 miles (33 km) |

* Maximum distance is limited to optical loss of the fiber and any additional loss by connectors, splices, and patch panels.

Table B: Product Compatibility Chart

| TRANSMITTER | COMPATIBLE RECEIVER |
| --- | --- |
| FVT120D8M1 | FVR120D8M1 |
| FVT120D8S1 | FVR120D8S1 |

## END OF SECTION