DIVISION 27 21 29

Model CNGE2FE16MS 18-PORT GIGABIT MANAGED ETHERNET SWITCH

ENGINEERING SPECIFICATION

# PART 1 - GENERAL

1.01 SUMMARY

- Eighteen  Port Gigabit Ethernet Managed Switch

1.02 SECTION INCLUDES

- CNGE2FE16MS-Series Gigabit Ethernet Managed Switch

1.03 REFERENCES

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- European Union Compliance (CE)

- NEMA TS2-1998

- CALTRANS

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide 16 (sixteen) 10/100TX RJ-45 ports, and 2 (two) combo 10/100/1000TX RJ-45 ports / Gigabit SFP ports.  The use of an SFP port disables the corresponding 10/100/1000TX RJ-45 port.  Similarly, the use of a 10/100/1000TX RJ-45 port disables the corresponding SFP port.

- The switch shall have SFP ports that permit the use of SFP modules for flexibility in determining optical operating wavelength, transmission distance, number of fibers, type of optical connector/receptacle, and the type of fiber.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of device specified.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate- controlled environment. Storage temperature not to exceed -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +75˚ C without the assistance of fan/forced-air cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95%, non-condensing. If the product is to be installed in humidity-with-condensation conditions, add suffix –C to the part number for optional conformal coating.

1.08 WARRANTY

- The switch shall be provided with the standard ComNet Communication Networks Comprehensive Lifetime Warranty: ComNet warrants the product to be free of factory defects under the manufacturers Lifetime Warranty as submitted under article 1.05 (A).

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer: ComNet Communication Networks; 3 Corporate Drive; Danbury CT 06810 USA; Telephone: 203-796-5300; Fax 203-796-5303; Email: sales@comnet.net; Internet: www.comnet.net

- Substitutions: Not Permitted

- All fiber optic Ethernet managed switches and SFP modules shall be supplied from a single manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

  - GENERAL SPECIFICATIONS

- The Ethernet managed switch system shall be a ComNet CNGE2FE16MS.  The switch shall support transmission utilizing Category 5 cable or better, or multimode or single-mode optical fiber.  The switch shall support IEEE 802.3 protocol using auto-negotiating and auto-MDI/MDI-X features.  The switch shall provide 16 (sixteen) 10/100TX RJ-45 ports, and 2 (two) combo 10/100/1000TX RJ-45 ports / Gigabit SFP ports.  The use of an SFP port shall disable the corresponding 10/100/1000TX RJ-45 port.  Similarly, the use of a 10/100/1000TX RJ-45 port shall disable the corresponding SFP port.  The module shall require no in-field electrical or optical adjustments or in-line optical attenuators, so as to ease installation.  The module shall provide power, link speed, and fiber port status indicating LED’s for monitoring proper switch and network operation.  The switch shall provide automatic re-settable solid-state current limiters on each switch, to reduce the chance of a single point of failure of the switch.  The switch shall provide redundant power supply capability to reduce the possibility of a single point of failure in the event of a failure of the prime power supply unit.  A serial data connection shall be provided for local management of the switch.  The switch shall be provided with a lifetime warranty, to reduce the users system life cycle cost in an event of a switch failure.

- The following IEEE Networking Standards shall be supported:

IEEE 802.3 10Base-T Ethernet

IEEE 802.3u 100Base-TX Fast Ethernet

IEEE 802.3ab 1000Base-TX

IEEE 802.3z Gigabit Ethernet Fiber

IEEE 802.3x Flow Control and Back-pressure

IEEE 802.1p Class of Service

IEEE 802.1Q VLAN and GVRP

IEEE 802.1D-2004 Rapid Spanning Tree  Protocol (RSTP)

IEEE802.3ad LACP

IEEE802.1X Port_based Network Access Control

- Switching Performance

Switch Technology: Store and Forward Technology with 32Gbps switch fabric.

System Throughput: 14,880pps for 10M Ethernet; 148,800pps for 100M Fast Ethernet; 1,488,100 for Gigabit Ethernet

Transfer Packet Size: 64 bytes to 1522 bytes (with VLAN Tag)

MAC Address: 8K MAC

Packet Buffer: 1Mbits

Relay Alarm: Dry relay contact output with 1A@24V resistive load capability

- MANAGEMENT

Configuration: Web, HTTPS, SSH, TFTP/Web Update for firmware and configuration backup/restore, DHCP Client, Warm reboot, Reset to

default, Admin password, Port Speed/Duplex control, status, statistic, MAC address table display, Static MAC, Aging time, SNMP v1, v2c, v3, Traps and RMON1.

SNMP MIB: MIB-II, Bridge MIB, VLAN MIB, SNMP MIB, RMON and Private MIB

Port Trunk: Up to 5 Static Trunk and 802.3ad LACP

VLAN: IEEE802.1Q VLAN, GVRP. Up to 64 VLAN groups

Quality of Service: Four priority queues per port,

IEEE802.1p COS and Layer 3 TOS/DiffServ

IGMP Snooping: IGMP Snooping V1/V2 for multicast filtering and IGMP Query

Rate Control: Ingress filtering for Broadcast, Multicast, Unknown DA or all packets, and Egress filtering for all packets

NTP: Network Time Protocol to synchronize time from Internet

Embedded Watchdog: Embedded hardware watchdog

timer to auto reset system when switch system failure

Port Mirroring: Online traffic monitoring on multiple selected ports

Port Security: Assign authorized MAC to specific port

SSH/SSL (128-bit encryption):

Support Secure Sockets Layer to protect the data

access from WEB browser, compliant with SSL

V2, V3 and TLS V1.0; Support Security Shell for

Telnet and compliant with SSH-V2 Perform with

RFC 4252, RFC 4253 and RFC 4254

IP Security: IP security to prevent unauthorized access

802.1x: Port_based Network Access Control

DHCP Server: Can assign 255 IP address, support IP and MAC binding

System Log: Supports both Local mode and Server mode

F. NETWORK REDUNDANCY

In addition to including the latest revision of rapid spanning tree, the switch shall provide X-Ring II dual-homing/coupled-ring topology for full network redundancy back-up, with a recovery time of less than 10 ms. The

X-Ring II shall provide very rapid automatic recovery in the event the network suffers a corruption or break in any of the transmission paths between X-Ring II-compatible switches within the ring. Using X-Ring II, up to 250 CNGE2FE16MS switches may be configured within a single ring or loop, as well as in a multiple coupled-ring topology. In the dual-homing mode, up to 50 switches may be located within the ring. The overall length or transmission distance of the ring shall be limited only by the SFP selected.

Multiple X-Rings may be created by the use of multiple head-end switches.

The X-Ring II configuration shall be established two ways. It may be determined manually by the user through the internal web interface, by designating one CNGE2FE16MS switch as the “Master”, and this shall be the switch that supervises and controls the flow of Ethernet traffic within the overall ring. The other switches within the ring shall be automatically designated as “Slaves”. Alternately, the master switch may be automatically selected by the user; the switch with the lowest MAC address becomes the master, and the remaining switches revert or default to slave status. Regardless as to how the X-Ring II configuration is established, should the master switch fail or lose its prime operating power, another slave switch within the ring shall automatically assume operation as the Master, and the communications within the ring continues with minimal interruption, with a maximum disruption or recovery time of <10 ms.

Rapid Spanning Tree Protocol: IEEE802.1D-2004 Rapid Spanning Tree Protocol.

Compatible with Legacy STP and IEEE802.1w.

Rapid Super Ring (RSR): Ring Redundancy Technology.

Failure recovery within 10 ms.

Dual Homing II: Multiple uplink paths to upper switches

Multiple Ring: Couple or multiple Rapid Super Rings

Legacy Super Ring: Backward compatible in client mode

Any Ring: Inter-operate with other vendors' ring Interface

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE802.3

- Data Rate: up to 1000 Mbps

- Data Inputs/Outputs: up to 16

- Operation Mode: Half or Full Duplex

2.05 OPTICAL SPECIFICATIONS

- Comnet Model Number CNGE2FE16MS

- Number of Optical ports: 2 (two) SFP-based

- Number of Optical Fibers Required: 1 or 2, SFP-dependent

- Optical Wavelength: 1310 or 1550 nm, SFP-dependent

- Optical Power Budget: SFP-dependent

- Maximum Optical Transmission Distance: up to 120 km (70 miles) singlemode, SFP-dependent

2.06 STATUS INDICATORS

- Power: Operating Power Applied; Green

- RJ-45 Link/Data: Green,  No Link/No Data: Off

- SFP Link/Data: Green, No Link/No Data: Off

2.07 CONNECTORS

- Optical: LC or SC, SFP-dependent

- Power:  Screw Clamp Terminal Strip.

- Data: RJ-45

- Console Port: RJ-45, serial communication.

2.08 ELECTRICAL SPECIFICATIONS

- Power:

+12 to +48VDC, 10.6 watts maximum power   consumption

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Independent voltage regulators on each board

- Circuit Board: UL 94 flame-rated and meets all IPC standards.

- IPv6 support dual stack for IPv4 and IPv6 support

- Plug and Play function: IPv6 Logo Committee

certified performance with the following RFCs:

- • RFC 2460 – IPv6 Specification

- • RFC 4861 – Neighbor Discovery for IPv6

- • RFC 4862 – IPv6 Stateless Address Auto-configuration

- • RFC 1981 – Path MTU Discovery for IPv6

2.09 MECHANICAL SPECIFICATIONS

- 17.3 in (W) x 11.0 in (D) x 1.7 in (H)		440 mm (W) x 280 mm (D) x 44 mm (H)

- Finish: The switch shall be constructed of an aluminum enclosure with a powder coat finish.

- Weight: <2 lb/1kg

2.10 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C

- Storage Temp: -40˚ C to +85˚ C

- Relative Humidity: 0% to 95%, non-condensing.

2.11 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Underwriters Laboratory (UL): Listing Number I.T.E. 6D16

- Underwriters Laboratory Canada (ULC): Listing Number I.T.E. 6D16

- UL 94-flame-rated PCB board: 94VO

PART 3 - EXECUTION

3.01 EXAMINATION

- All optical connectors on the switch shall be protected with dust caps, and these caps shall remain in place until the mating cable connectors are connected to the switch.

3.02 PREPARATION

- Optical Fiber

- Caution: NEVER look into the end of an active optical fiber when using laser optical emitters. Eye damage can occur. Wear eye protection when cleaving, terminating, and splicing fiber.

- The number and type of optical fiber shall meet the requirements of the ComNet model number as defined in article 2.05 and as used in the installation.

- All optical fiber cables shall be properly installed and terminated with the mating optical connectors as defined in article 2.07 (A).

- The optical link shall be tested, at a minimum, with a power meter,  or an OTDR to ensure the link budget (overall optical path loss) plus an added 3dB of optical safety margin, does not exceed the optical power budget as submitted in article 2.05.

- All optical connectors installed on the optical fiber shall be cleaned in accordance with the optical connector manufacturer’s specifications, and protected with dust caps. These caps shall remain in place until the mating cable connectors are connected to the switch.

3.03 INSTALLATION

- General: Locate the switches as indicated on the approved detail drawings and install the switch in accordance with the ComNet installation and operation manual.

3.04 TESTING

- Testing the fiber optic Ethernet link.

- Verify that the data connectors and optical fibers are properly connected.

- Make sure that power is applied to all switches, controllers, and receiver drivers or other equipment used in the network.

- Successful switch operation should be confirmed at this point by communications with other equipment connected within the network.

3.05 CLEANING

- Follow all instructions for the proper use of any solvents and adhesives used for the termination and splicing of optical fiber.

- At the completion of the installation, properly dispose of all fiber scraps.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| CNGE2FE16MS PORTS† | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| CNGE2FE16MS ports 1 through 16 | Electrical 10/100TX, IEEE 802.3 | 320 ft (100 m) |
| CNGE2FE16MS combo ports 17 and 18 | Any combination of Electrical 10/100/1000 TX using Category 5 cable or better, and/or Optical 1000Base FX via SFP module using multimode or single-mode fiber | Electrical: 320 ft (100 m) Optical: Multimode, SFP-dependent up to 550 meters Single-mode, SFP-dependent up to 70 miles (120 km) |

* Maximum range will be limited by optical loss of the fiber, connectors, and splices.

Table B: Product Compatibility Chart

| CNGE2FE16MS | Compatible ComNet Ethernet Devices |
| --- | --- |
| CNGE2FE16MS ports 1 through 16 | CNGE3FE7MS2: RJ-45 Ports 1 through 6 & 8. Combo ports 7, 9, and 10: RJ-45 Ports, 10/100/1000 Mbps; or SFP ports, 100/1000 Mbps CNFE2MC, CNFE2MC-M CNFE22MC CNFE1002M1A, CNFE1002M1B, CNFE1002M1A-M, CNFE1002M1B-M CNFE1002S1A, CNFE1002S1B, CNFE1002S1A-M, CNFE1002S1B-M CNFE1003M2, CNFE1003M2-m CNFE1003S2, CNFE1003S2-m Or any Ethernet device that meets the IEEE 802.3 10/100 TX protocols |
| CNGE2FE16MS combo ports 17 and 18 | CNGE2MC, CNGE2MC-M Compatible with any Ethernet device that meets IEEE 802.3 1000Base TX protocols, as well as any Ethernet device that meets the requirements of IEEE 802.1 |