DIVISION 27 21 29

CNGE8FX4TX4MS –EIGHT PORT FIBER OPTIC GIGABIT ETHERNET MANAGED SWITCH

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- Ten Port Gigabit Ethernet Managed Switch

1.02 SECTION INCLUDES

- CNGE8FX4TX4MS Series Ethernet Managed Switch

1.03 REFERENCES

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- European Union Compliance (CE)

- NEMA TS2-1998

- CALTRANS

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide 4 (four) 10/100/1000TX RJ-45 ports, 4 (four) 10/100/1000TX RJ-45 ports, and 4 (four) Gigabit SFP ports.  Use of an SFP port disables the corresponding 10/100/1000TX RJ-45 port.  Similarly, use of a 10/100/1000TX RJ-45 port disables the corresponding SFP port.

- The system shall have SFP ports allowing for the use of SFP modules for flexibility in determining operating wavelength, range, number of fibers, type of receptacle, and type of fiber.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of device specified.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment. Storage Temperature not to exceed -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing). If product is installed in condensation conditions, add –C to the part number.

1.08 WARRANTY

- Standard Communication Networks Comprehensive Lifetime Warranty: ComNet warrants the product to be free of factory defects under manufacture’s Lifetime Warranty as submitted under article 1.05 (A).

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer: Communication Networks; 3 Corporate Drive; Danbury CT 06810 USA; Telephone: 203-796-5300; Fax 203-796-5303; Email: sales@ComNet.net; Internet: www.ComNet.net

- Substitutions: Not Permitted

- All fiber optic Ethernet managed switches and SFP modules shall be supplied from a single manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

  - GENERAL SPECIFICATIONS

- The Ethernet managed switch system shall be a ComNet CNGE8FX4TX4MS.  The module shall support transmission utilizing Category 5 cable or better, multimode, or single-mode fiber.  The module shall support the Ethernet data IEEE 802.3 protocol using Auto-negotiating and Auto-MDI/MDI-X features.  The module shall feature 4 (four) 10/100/1000TX RJ-45 ports, 4 (four) 10/100/1000TX RJ-45 ports, and 4 (four) Gigabit SFP ports.  Use of an SFP port disables the corresponding 10/100/1000TX RJ-45 port.  Similarly, use of a 10/100/1000TX RJ-45 port disables the corresponding SFP port.  The module shall require no in-field electrical or optical adjustments or in-line attenuators to ease installation.  The module shall provide power, link speed, and fiber port status indicating LED’s for monitoring proper system operation.  The modules shall provide automatic re-settable solid-state current limiters on each module to reduce the chance of a single point failure of the system.  The module shall have redundant power supply connections to minimize single point failure.  The module shall provide a serial connection for local management of the device.  The module shall have a lifetime warranty to reduce system life cycle cost in an event of a module failure.

- The following IEEE Networking Standards shall be supported:

IEEE802.3 10Base-T Ethernet

IEEE802.3u 100Base-TX

IEEE802.3ab 1000Base-T

IEEE802.3z Gigabit fiber

IEEE802.3x Flow Control and Back Pressure

IEEE802.3ad Port trunk with LACP

IEEE802.1d Spanning Tree/ IEEE802.1w Rapid Spanning Tree

IEEE802.1p Class of Service

IEEE802.1Q VLAN Tag

IEEE802.1x User Authentication (Radius)

- Switching Performance

Switch Technology: Store and Forward Technology with 16Gbps Switch Fabric.

Packet throughput ability: (Full Duplex): 23.8Mpps @64bytes

Transfer Packet Size: 64 bytes to 1522 bytes (with VLAN Tag)

MAC Address: 8K MAC

Packet Buffer: 1Mbits

Relay Alarm: Dry Relay output with 1A@24V ability

- MANAGEMENT

SNMP v1 v2c, v3/ Web/Telnet/CLI/NS-View

Management

SNMP MIB RFC 1215 Trap, RFC1213 MIBII, RFC 1157 SNMP,MIB, RFC 1493 Bridge MIB, RFC 2674 VLAN MIB, RFC 1643 , RFC 1757, RSTP MIB, Private MIB

VLAN Port Based VLAN

IEEE 802.1Q Tag VLAN (256 entries)/ VLAN ID (Up to 4K, VLAN ID can be assigned from 1 to 4096.) GVRP (256 Groups) Double Tag VLAN (Q in Q) - Optional

Port Trunk w/ LACP LACP Port Trunk: 4 Trunk groups/Maximum 4 trunk members

Spanning Tree Support IEEE802.1d Spanning Tree and IEEE802.1w Rapid Spanning Tree

X-Ring Support X-Ring, Dual Homing and Couple Ring Topology Provide redundant backup feature and the recovery time below 20ms

Quality of Service The quality of service determined by port, Tag and IPv4 Type of service, IPv4/ IPv6 Different Service

Class of Service Support IEEE802.1p class of service, per port provides 4 priority queues

Port Security Support 100 entries of MAC address for static MAC and another 100 for MAC filter

Port Mirror Support 3 mirroring types: RX, TX and Both packet

IGMP Support IGMP snooping v1,v2 256 multicast groups and IGMP query

IP Security Supports 10 IP addresses that have permission to access the switch management and to prevent unauthorized intruder. Login Security

Support IEEE802.1X Authentication/RADIUS

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE802.3

- Data Rate: up to 1000 Mbps

- Data Inputs/Outputs: up to 8

- Operation Mode: Half or Full Duplex

2.05 OPTICAL SPECIFICATIONS

- ComNet Model Number CNGE8FX4TX4MS

- Number of Optical ports: up to 4 SFP-based

- Number of Fibers Required: 1 or 2, SFP-dependant

- Optical Wavelength: 1310 or 1550 nm, SFP-dependant

- Optical Power Budget: SFP-dependant

- Maximum Distance: up to 120 km (70 mi) single mode, SFP-dependant

2.06 STATUS INDICATORS

- Power: Proper Power = Green

- RJ-45 Link/Data: Green,  No Link/No Data: Off

- SFP Link/Data: Green, No Link/No Data: Off

2.07 CONNECTORS

- Optical: LC or SC, SFP-dependant

- Power:  Screw Clamp Terminal Strip.

- Data: RJ-45

- Console: RJ-45 serial communication.

2.08 ELECTRICAL SPECIFICATIONS

- Power:

12VDC to 24VDC @ 1A maximum

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

- Circuit Board: UL 94 flame rated and meets all IPC standards.

2.09 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions: 4.84” x 3.78” x 5.43” (123 mm x 96 mm x 138 mm)

- Finish: Module shall be constructed of a metal enclosure with a powder coat.

- Weight: <2 lb/1kg

2.10 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C

- Storage Temp: -40˚ C to +85˚ C

- Relative Humidity: 0% to 95% (non-condensing).

2.11 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Underwriters Laboratory (UL) Listing Number: I.T.E. 6D16

- Underwriters Laboratory Canada (ULC) Listing Number: I.T.E. 6D16

- UL 94-flame rated PCB board: 94VO

2.12 ACCESSORIES

- Wall mount bracket automatically included

- DIN Rail back mount automatically included

PART 3 - EXECUTION

3.01 EXAMINATION

- All optical connectors shall be covered with dust caps and remain on the module until installing cable connectors to module.

3.02 PREPARATION

- DIN Rail Mount Module

- Shall be mounted on a properly installed DIN Rail adequate for the size and weight of the module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet mounting template and installation manual.

- Wallmount (Surface Mount) Module

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet mounting template and installation manual.

- Optical Fibers

- Caution: NEVER look into the end of an active optical fiber when using laser light output. Eye damage can occur. Wear eye protection when cleaving, terminating, and splicing fiber.

- The number and type of optical fiber shall meet the requirements of the ComNet model number in article 2.05 used in the installation.

- All optical fiber cables shall be properly installed and terminated with the mating optical connectors as submitted in article 2.07 (A).

- The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3dB of optical safety margin does not exceed the optical power budget as submitted in article 2.05.

- All optical connectors on cable shall be cleaned in compliance to optical connector manufactures specifications and covered with dust caps until connection to the fiber optic module.

3.03 INSTALLATION

- General: Locate fiber optic modules as indicated on the approved detail drawings and install module in compliance with the ComNet installation and operations manual.

3.04 TESTING

- Testing the Fiber Optic Ethernet Link.

- Verify that the data leads and optical fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, controllers, and receiver drivers or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

3.05 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all fiber scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| CNGE8FX4TX4MS PORTS† | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| CNGE8FX4TX4MS ports 1 through 4 | Electrical 10/100/1000TX | 320 ft (100 m) |
| CNGE8FX4TX4MS ports 5 through 8, non-SFP electrical | 10/100/1000 TX via Category 5 cable or better, any combination of Electrical 10/100/1000 | Electrical: 320 ft (100 m) |
| CNGE8FX4TX4MS ports 5 through 8, SFP optical | TX via 10/100/1000TX SFP module using Category 5 cable or better, and/or Optical 1000Base FX via SFP module using single mode fiber | Electrical: 320 ft (100 m) Optical, single mode: SFP-dependant up to 70 mi (120 km) |

* Maximum range will be limited by optical loss of the fiber, connectors, and splices.

Table B: Product Compatibility Chart

| CNGE8FX4TX4MS PORTS | COMPATIBLE DEVICES |
| --- | --- |
| CNGE8FX4TX4MS ports 1 through 4 | CNGE8FX4TX4MS, ports 1 through 4 CNFE10MS, ports 1 through7, ports 8 through 10 non-SFP CNFE2MC, CNFE2MC-M CNFE22MC CNFE1002M1A, CNFE1002M1B, CNFE1002M1A-M, CNFE1002M1B-M CNFE1002S1A, CNFE1002S1B, CNFE1002S1A-M, CNFE1002S1B-M CNFE1003M2, CNFE1003M2-m CNFE1003S2, CNFE1003S2-m And device that meets IEEE 802.3 10/100 TX protocols |
| CNGE8FX4TX4MS ports 5 through 8 – non-SFP electrical | CNGE8FX4TX4MS, ports 5 through 8 CNGE2MC, CNGE2MC-M Any device that meets IEEE 802.3 1000Base TX protocols |
| CNGE8FX4TX4MS ports 5 through 8 – SFP electrical | CNGE8FX4TX4MS, ports 1 through 8 CNGE2MC, CNGE2MC-M Any device that meets IEEE 802.3 1000Base TX protocols |
| CNGE8FX4TX4MS ports 5 through 8 – SFP optical | CNGE8FX4TX4MS, ports 8 through 10 CNGE2MC, CNGE2MC-M Any device that meets IEEE 802.3u 1000Base FX protocols |

## END OF SECTION