DIVISION 27 21 29

CNGE8MS – EIGHT PORT FIBER OPTIC GIGABIT ETHERNET MANAGED SWITCH

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- Eight Port Gigabit Ethernet Managed Switch

1.02 SECTION INCLUDES

- CNGE8MS Series Ethernet Managed Switch

1.03 REFERENCES

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- European Union Compliance (CE)

- NEMA TS2-1998

- CALTRANS

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide 4 (four) 10/100/1000T(X) RJ-45 ports and 4 (four) combo 10/100/1000T(X) RJ-45 ports and 100/1000FX ports.  Use of an SFP port disables the corresponding 10/100/1000TX RJ-45 port.  Similarly, use of a 10/100/1000TX RJ-45 port disables the corresponding SFP port.

- The system shall have SFP ports allowing for the use of SFP modules for flexibility in determining operating wavelength, range, number of fibers, type of receptacle, and type of fiber.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of device specified.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment. Storage Temperature not to exceed -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing). If product is installed in condensation conditions, add /C to the part number.

1.08 WARRANTY

- Standard Communication Networks Comprehensive Lifetime Warranty: Comnet warrants the product to be free of factory defects under manufacture’s Lifetime Warranty as submitted under article 1.05 (A).

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer: Communication Networks; 3 Corporate Drive; Danbury CT 06810 USA; Telephone: 203-796-5300; Fax 203-796-5303; Email: sales@comnet.net; Internet: www.comnet.net

- Substitutions: Not Permitted

- All fiber optic Ethernet managed switches and SFP modules shall be supplied from a single manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

  - GENERAL SPECIFICATIONS

- The Ethernet managed switch system shall be a ComNet CNGE8MS.  The module shall support transmission utilizing Category 5 cable or better, multimode, or single-mode fiber.  The module shall support the Ethernet data IEEE 802.3 protocol using Auto-negotiating and Auto-MDI/MDI-X features.  The module shall feature 4 (four) 10/100/1000T(X) RJ-45 ports and 4 (four) combo 10/100/1000T(X) RJ-45 ports / 100/1000FX ports.  Use of an SFP port disables the corresponding 10/100/1000TX RJ-45 port.  Similarly, use of a 10/100/1000TX RJ-45 port disables the corresponding SFP port.  The module shall require no in-field electrical or optical adjustments or in-line attenuators to ease installation.  The module shall provide power, link speed, and fiber port status indicating LED’s for monitoring proper system operation.  The modules shall provide automatic re-settable solid-state current limiters on each module to reduce the chance of a single point failure of the system.  The module shall have dual redundant power supply connections to minimize single point failure.  The module shall provide a serial connection for local management of the device.  The module shall have a lifetime warranty to reduce system life cycle cost in an event of a module failure.

- The following IEEE Networking Standards shall be supported:

IEEE 802.3 10Base-T Ethernet

IEEE 802.3u 100Base-TX Fast Ethernet

IEEE 802.3ab 1000Base-TX

IEEE 802.3z Gigabit Ethernet Fiber

IEEE 802.3x Flow Control and Back-pressure

IEEE 802.3AB LLDP

IEEE 802.1p class of service

IEEE 802.1Q VLAN and GVRP

IEEE 802.1D Spanning Tree Protocol

IEEE 802.1w Rapid Spanning Tree Protocol (RSTP)

IEEE 802.1s Multiple Spanning Tree Protocol

IEEE802.3ad LACP

IEEE802.1x Port_based Network Access Control

- Switching Performance

Switch Technology: Store and Forward Technology with 16Gbps Switch Fabric.

System Throughput: 14,880pps for 10M Ethernet; 148,800pps for 100M Fast Ethernet; 1,488,100 for Gigabit Ethernet

Transfer Packet Size: 64 bytes to 1522 bytes (with VLAN Tag)

MAC Address: 8K MAC

Packet Buffer: 1Mbits

Relay Alarm: Dry Relay output with 1A@24V ability

- MANAGEMENT

Configuration: Web, HTTPS, SSH,TFTP/Web Update for firmware and configuration backup/restore, DHCP Client, Warm reboot, Reset to

default, Admin password, Port Speed/Duplex control, status, statistic, MAC address table display, Static MAC, Aging time, SNMP v1, v2c, v3, Traps and RMON1.

SNMP MIB: MIB-II, Bridge MIB, VLAN MIB, SNMP MIB, RMON and Private MIB

Port Trunk: Up to 4 Static Trunks and 802.3ad LACP

VLAN: IEEE802.1Q VLAN, GVRP. Up to 4096 VLAN groups

Quality of Service: Four priority queues per port,

IEEE802.1p COS and Layer 3 TOS/DiffServ

IGMP Snooping: IGMP Snooping v2/v3 for multicast filtering and IGMP Query

Rate Control: Ingress filtering for Broadcast, Multicast, Unknown DA or all packets, and Egress filtering for all packets

NTP: Network Time Protocol to synchronize time from Internet

Embedded Watchdog: Embedded hardware watchdog

timer to auto reset system when switch system failure

Port Mirroring: Online traffic monitoring on multiple selected ports

Port Security: Assign authorized MAC to specific port

IP Security: IP security to prevent unauthorized access

802.1x: Port_based Network Access Control

DHCP Server: Can assign 255 IP address, support IP and MAC binding

System Log: Supports both Local mode and Server mode

NETWORK REDUNDANCY

Rapid Spanning Tree Protocol: IEEE802.1w

Compatible with Legacy STP: IEEE802.1D

Multiple Spanning Tree Protocol: IEEE802.1s

C-Ring: Ring Redundancy Technology.

Failure recovery within 30ms for 250 units of connection.

Dual Homing: Multiple uplink paths to upper switches

Coupling Ring: Couple multiple C-Rings

C-RSTP: Complex network topologies with <20ms recovery.

Legacy Ring: Backward compatible in client mode with X-Ring based configurations

Com-Ring: Inter-operate with other vendors' ring interface

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE802.3

- Data Rate: up to 1000 Mbps

- Data Inputs/Outputs: up to 8

- Operation Mode: Half or Full Duplex

2.05 OPTICAL SPECIFICATIONS

- ComNet Model Number CNGE8MS

- Number of Optical ports: up to 4 SFP-based

- Number of Fibers Required: 1 or 2, SFP-dependant

- Optical Wavelength: 850, 1310 or 1550 nm, SFP-dependant

- Optical Power Budget: SFP-dependant

- Maximum Distance: up to 120 km (70 mi) singlemode, SFP-dependant

2.06 STATUS INDICATORS

- Power 1-2: Proper Power = Green

- R.M.: C-Ring Master = Green

- Ring: Ring Enabled = Green

- Fault: Fault Present = Amber

- RJ-45 Link/Data: Green,  No Link/No Data: Off

- SFP Link/Data: Green, No Link/No Data: Off

2.07 CONNECTORS

- Optical: LC or SC, SFP-dependant

- Power:  Screw Clamp Terminal Strip

- Data: RJ-45

- Console: RJ-45 serial communication.

2.08 ELECTRICAL SPECIFICATIONS

- Power:

Two Redundant 12VDC to 48VDC @ 25W maximum input

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

- Circuit Board: UL 94 flame rated and meets all IPC standards.

2.09 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions: 2.93” x 4.3” x 6.05” (74 mm x 109 mm x 153 mm)

- Finish: Module shall be constructed of a metal enclosure.

- Weight: <3 lb/1.1kg

2.10 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C

- Storage Temp: -40˚ C to +85˚ C

- Relative Humidity: 0% to 95% (non-condensing).

2.11 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Underwriters Laboratory (UL) Listing Number: I.T.E. 6D16

- Underwriters Laboratory Canada (ULC) Listing Number: I.T.E. 6D16

- UL 94-flame rated PCB board: 94VO

2.12 ACCESSORIES

- Wall mount bracket automatically included

- DIN Rail back mount automatically included

- Console cable automatically included

PART 3 - EXECUTION

3.01 EXAMINATION

- All optical connectors shall be covered with dust caps and remain on the module until installing cable connectors to module.

3.02 PREPARATION

- DIN Rail Mount Module

- Shall be mounted on a properly installed DIN Rail adequate for the size and weight of the module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the Comnet mounting template and installation manual.

- Wall-mount (Surface Mount) Module

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the Comnet mounting template and installation manual.

- Optical Fibers

- Caution: NEVER look into the end of an active optical fiber when using laser light output. Eye damage can occur. Wear eye protection when cleaving, terminating, and splicing fiber.

- The number and type of optical fiber shall meet the requirements of the Comnet model number in article 2.05 used in the installation.

- All optical fiber cables shall be properly installed and terminated with the mating optical connectors as submitted in article 2.07 (A).

- The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3dB of optical safety margin does not exceed the optical power budget as submitted in article 2.05.

- All optical connectors on cable shall be cleaned in compliance to optical connector manufactures specifications and covered with dust caps until connection to the fiber optic module.

3.03 INSTALLATION

- General: Locate fiber optic modules as indicated on the approved detail drawings and install module in compliance with the Comnet installation and operations manual.

3.04 TESTING

- Testing the Fiber Optic Ethernet Link.

- Verify that the data leads and optical fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, controllers, and receiver drivers or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

3.05 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all fiber scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| CNGE8MS PORTS† | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| CNGE8MS ports 1 through 4 | Electrical 10/100/1000T(X) | 320 ft (100 m), Cat 5e or better |
| CNGE8MS ports 5 through 8, non-SFP electrical | Electrical 10/100/1000T(X) | 320 ft (100 m), Cat 5e or better |
| CNGE8MS ports 5 through 8, SFP optical | any combination of Optical 100Base-FX or 1000Base-FX via SFP module using multimode or singlemode fiber | SFP-dependant up to 70 mi (120 km) on single-mode fiber |

* Maximum range will be limited by optical loss of the fiber, connectors, and splices.

Table B: Product Compatibility Chart

| CNGE8MS PORTS | COMPATIBLE DEVICES |
| --- | --- |
| CNGE8MS Copper ports 1 through 8 | Devices that meet IEEE 802.3 10/100/1000Base T(X) protocols |
| CNGE8MS SFP ports 5 through 8 | Devices that meet IEEE 802.3 100/1000Base FX protocols |

## END OF SECTION