DIVISION 27 16 16

CNFE3DOE2/M – RS232/422/485 Data over Ethernet Terminal Server/Media Converter

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- Data over Ethernet Terminal Server/Media Converter

1.02 SECTION INCLUDES

- CNFE3DOE2/M Data Terminal Server

1.03 REFERENCES

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide any combination of two RS-232, RS-422, or 2 or 4-wire RS-485 serial data circuits to be inserted onto any 10/100 Mbps Ethernet-based network.

- The system shall utilize 1310/1550 nm optics capable of simultaneous bi-directional digital data transmission on one or two multimode optical fibers. (SFP dependent)

- The system shall utilize 1310/1550 nm optics capable of simultaneous bi-directional data transmission on one or two single mode optical fiber. (SFP dependent)

1.05 SUBMITTALS

- Product Data: Manufacturer’s printed product data sheet.

- Detail Drawings: Electrical and optical connect drawings. Product mounting template.

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information.

- Warranty: Manufacturer’s Printed Warranty

1.06 DELIVERY, STORAGE AND HANDLING

- Deliver materials in unopened factory packaging with Manufacturer’s bar coding to the job site.

- Inspect product upon delivery to assure that specified products have been received.

- Store in original packaging in a climate-controlled environment. Storage Temperature not to exceed: -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing). If product is installed in condensation conditions above 95%, unit shall have conformal coating applied to the printed circuit board (apply -C to part number).

1.08 WARRANTY

- Standard Communication Networks Comprehensive Lifetime Warranty: ComNet warrants the product to be free of factory defects under manufacture’s Lifetime Warranty as submitted under article 1.05 (D)

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer: Communication Networks, Inc.; 3 Corporate Drive, Danbury, CT 06810 USA; Telephone: 203-796-5300; Fax 203-796-5303; Email: sales@ComNet.net  Internet: www.ComNet.net

- Substitutions: Not Permitted

- All fiber optic modules shall be supplied from a single manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

2.03 GENERAL SPECIFICATIONS

- The Data Terminal Server shall be a ComNet CNFE3DOE2/M product.  The product shall support the transmission of any combination of two RS-232, RS-422, or 2 or 4-wire RS-485 serial data circuits to be inserted onto any 10/100 Mbps Ethernet-based network. The module shall be transparent to data protocols used by various manufactures, providing for universal compatibility should future system expansion or changes be required. The module shall require no in-field electrical or optical adjustments or in-line attenuators to ease installation. The module shall provide receive data, transmit data, and optical carrier detect status indicating LED’s for monitoring proper system operation. The modules shall provide automatic re-settable solid-state current limiters and independent voltage regulators on each module to reduce the chance of a single point failure of the system. The module shall have an MTBF of >100,000 hours and operate in an environment of –40˚ C to +75˚ C and relative humidity between 0% to 95% (non-condensing). The module shall be UL and ULC listed. The circuit board shall meet all IPC standards. All PC boards shall be designated with part number, PC board number and show appropriate revision number. Housing shall be of all metal construction. All LED indicators and both electrical and mechanical connections shall be identified with silk-screened labels. The module shall have a lifetime warranty to reduce system life cycle cost in an event of a module failure.

2.04 DATA SPECIFICATIONS

- Data Interface: RS232/RS422/RS485, Hardware Handshaking, RS485 2-wire/4-wire

- Data Rate: 2400 to 230,000 bps

- Operation Mode: Asynchronous, Simplex or Full Duplex

- Ethernet: 10/100TX, 100FX

- Access one serial device from the Internet and another serial device from a local area network (LAN) using SSH or SSL

- Serial data appearing on either of the two serial data ports is converted to Ethernet, and transmitted to either the SFP and/or RJ45 ports. The unit can also act as a media converter, for converting copper to fiber.

- Bit Error Rate:  <1 in 10-9 @ Maximum

Optical Loss Budget (SFP dependent)

2.05 OPTICAL SPECIFICATIONS

- ComNet Model Number CNFE3DOE2/M

- Number of Optical ports: 1 SFP-based

- Number of Fibers Required: 1 or 2, SFP-dependent

- Optical Wavelength:1310 or 1550 nm, SFP dependent

- Optical Power Budget: SFP-dependent

- Maximum Distance: up to 80 km (50 mi) single-mode, SFP-dependent

- Number of Fibers Required: 1 or 2 single or multi-mode SFP dependent

- Optical Attenuation: No manual adjustments required

2.06 STATUS INDICATORS

- Power

- Ethernet

2.07 CONNECTORS

- Optical: 1 × SFP pluggable optics

- Ethernet: 2 × RJ-45

- Power: Screw Terminal Block

- Data:  Terminal Block with Screw Clamps

2.08 ELECTRICAL SPECIFICATIONS

- Power:  Dual 9-60 VDC @ 5W

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

2.09 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions:

5.4 × 2.2 × 2.9 in (13.7 × 5.5 × 7.4 cm)

- DIN Rail Mount Dimensions:

3.9 × 2.2 × 3.6 in (9.9 × 5.5 × 9.2 cm)

- Finish: Module shall be constructed of a metal enclosure with a powder coat finish model Number F63B12 with all connections and indicators silk-screened directly on unit. Rack mount units shall be constructed of anodized aluminum.

- Weight: 1.5lbs./0.68kg

2.10 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C

- Storage Temp: -40˚ C to +85˚ C

- Relative Humidity: 0% to 95% (non-condensing). If product is installed under condensation conditions, unit shall have conformal coating applied to the printed circuit board. (Add –C to model number for conformal coated printed circuit board)

2.11 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- Circuit board meets IPC Standard.

2.12 ACCESSORIES

- Panel Mounting Adapter Plate Kit with Mounting Hardware.

- Din Rail Mounting Adaptor Clip Kit with Mounting Hardware.

PART 3 - EXECUTION

3.01 EXAMINATION

- Inspect modules before installation.

- Modules shall be free of any cosmetic defects or damage.

- All optical connectors shall be covered with dust caps and remain on the module until installing cable connectors to module.

- Shipping box shall include the module and quick start guide.

3.02 PREPARATION

- CNFE3DOE2/M (Surface Mount)

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet mounting template and installation manual.

- CNFE3DOE2/M (DIN Rail)

- Shall be installed on a din rail capable of supporting weight of unit. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet installation manual.

- Management

- All configurations are done through its web server at a default address of 192.168.10.1 and default user name and password.

- Shall support the following: HTTP, HTTPS, SNMPv1 RFC1155, RFC1213 & RFC1215

- TCP, UDP, SSL and SSH

- Optical Fibers

- Caution: NEVER peer into the end of an active optical fiber when using laser light output. Eye damage can occur. Wear eye protection when cleaving, terminating, and splicing fiber.

- The number and type (multimode or single-mode) of optical fiber shall meet the requirements of the ComNet model number in article 2.05 used in the installation.

- All optical fiber cables shall be properly installed and terminated with the mating optical connectors as submitted in article 2.07 (A).

- The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3dB of optical safety margin does not exceed the optical power budget (SFP dependent).

- All optical connectors on cable shall be cleaned in compliance to optical connector manufactures specifications and covered with dust caps until connection to the fiber optic module.

3.03 INSTALLATION

- General: Locate CNFE3DOE3/M modules as indicated on the approved detail drawings and install module in compliance with the ComNet installation and operations manual.

3.04 TESTING

- Testing the Fiber Optic Data Link.

- Verify that the data leads and optical fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, controllers, and receiver drivers or other equipment used in the system.

- Successful data link operation should be confirmed at this point by try to communicate with connected equipment.

- Factory Default can be accomplished by selecting “Reset Factory Defaults” on web browser page or press the reset button on the device.

3.05 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all fiber scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| CNFE3DOE2/M PORTS | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| Ports 1 & 2 | Electrical 10/100Mbps TX (CAT5 or better cable) | 320ft (100m) |
| Port 3 Ports D1 & D2 | 10/100Mbps FX base via SFP Optical RS232/RS422/RS485 (22AWG TSP or better) | 50 mi (70 km) 4000ft (1219m) |

* Maximum distance is limited to optical loss of the fiber and any additional loss by connectors, splices and patch panels.

## END OF SECTION