DIVISION 27 21 29

CLFE(X)IPS SERIES – HIGH POWER MID-SPAN INJECTOR

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- Ethernet Injector

1.02 SECTION INCLUDES

- CLFE(X)IPS Series High Power Mid-Span Injector

1.03 REFERENCES

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide an Ethernet High Power Mid-Span Injector for 10/100/1000Mbps networks.

1.05 SUBMITTALS

- Product Data: Manufacturer’s printed product data sheet for each type of Transceiver specified.

- Detail Drawings: Electrical connect drawings. Product mounting template.

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of Transceiver specified.

- Warranty: Manufacturer’s Printed Warranty

1.06 DELIVERY, STORAGE AND HANDLING

- Deliver materials in unopened factory packaging with Manufacturer’s bar coding to the job site.

- Inspect product upon delivery to assure that specified products have been received.

- Store in original packaging in a climate controlled environment. Storage Temperature not to exceed: -30˚ C to +70˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of -10˚ C to +50˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing). If product is installed in condensation conditions, unit shall have conformal coating applied to the printed circuit board.

1.08 WARRANTY

- Standard Communication Networks Comprehensive Lifetime Warranty: ComNet warrants the product to be free of factory defects under manufacture’s Lifetime Warranty as submitted under article 1.05 (E)

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer: Communication Networks 3 Corporate Drive Danbury, CT 06810 USA; Telephone: 203-796-5300; Fax 203-796-5303; Email: sales@ComNet.net; Internet: www.ComNet.net

- Substitutions: Not Permitted

- All modules shall be supplied from a single manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

2.03 GENERAL SPECIFICATIONS

- The devices shall be 8 or 16 port high power PoE mid-span injectors. They shall compatible with 10/100/1000 BaseT Ethernet networks. 
They shall meet IEEE 802.3af and IEEE 802.3at standards and deliver up to 37W per port simultaneously on all ports without requiring power management. The PoE function shall be set up with Windows GUI or use a default plug and play option. These mid-span power injectors shall be equipped with LEDs to provide operational status. No IP settings or configurations are required and they shall be completely transparent to the Ethernet network and higher layer protocols. The modules shall be 1 RU high and can be easily installed in 19” racks. The devices shall be packaged in rugged aluminum housings and be designed for desktop or stand-alone mounting. The 8 channel and 16 channel systems shall be in an EIA 19” 1U high rack for easy installation. The module shall have an MTBF of >100,000 hours and operate in an environment of -10˚ C to +50˚ C and relative humidity between 0% to 95% (non-condensing). The module shall be UL and ULC listed and CE marked. The circuit board shall be UL 94 flame rated and meet all PCI standards.  All PC boards shall be designated with part number, PC board number and show appropriate revision number. Housing shall be of all metal construction.  All LED indicators and both electrical and mechanical connections shall be identified with silk-screened labels. The module shall have a Lifetime warranty to reduce system life cycle cost in an event of a module failure.

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE802.3

- Data Rate: 10/100/1000Mbps

- Operation Mode: Full or Half Duplex

2.05 STATUS INDICATORS

- Power

- Output

2.06 CONNECTORS

- Power: IEC380-8

- Data: RJ-45

2.07 ELECTRICAL SPECIFICATIONS

- Output Power: 52 VDC, 37W Max per Port

CLFE8IPS: 300W Max, aggregated

CLFE16IPS: 600W Max, aggregated

- Input Power: 110-240VAC, 50-60Hz @ 6.5A, max

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

- Circuit Board: UL 94 flame rated and meets all IPC standards.

2.08 MECHANICAL SPECIFICATIONS

- Rack Mount Dimensions: CLFE8IPS

1.75 × 17× 12 in, (4.45 × 43.2 × 30.5 cm)

Weight: 9.5lbs (4.3 kg)

- Rack Mount Dimensions: CLFE16IPS

1.75 × 17× 12 in, (4.45 × 43.2 × 30.5 cm)

Weight: 10.6lbs (4.8 kg)

- Finish: Module shall be constructed of a metal enclosure with all connections and indicators silk-screened directly on unit.

2.9 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: -10˚ C to +50˚ C

- Storage Temp: -30˚ C to +70˚ C

- Relative Humidity: 0% to 95% (non-condensing). If product is installed under condensation conditions, unit shall have conformal coating applied to the printed circuit board. (Add –C to model number for conformal coated printed circuit board)

2.10 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- UL 94-flame rated PCB board

- European Listed (CE)

PART 3 - EXECUTION

3.01 EXAMINATION

- Inspect modules before installation.

- Modules shall be free of any cosmetic defects or damage.

- Shipping box shall include the module, power supply and operations manual.

3.02 PREPARATION

- Standalone Module (Surface Mount)

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet mounting template and installation manual.

- Rack Mount Module (19” Rack)

- Ensure the card cage is installed in a standard EIA 19” (482.6 mm) rack or wall standoff bracket adequate for the size and weight of the card cage. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet installation manual.

3.03 INSTALLATION

- General: Locate modules as indicated on the approved detail drawings and install module in compliance with the ComNet installation and operations manual.

3.04 TESTING

- Testing the Ethernet Link.

- Verify that the data leads and signal leads are properly connected.

- Make sure that power is applied to all modules, controllers, and receiver drivers or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

3.05 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| CLFE(X)IPS SERIES | DESCRIPTION |
| --- | --- |
| CLFE8IPS CLFE16IPS | 8 Port High-Power PoE Mid-Span Injector 300 W Max Aggregated 16 Port High-Power PoE Mid-Span Injector 600 W Max Aggregated |

## END OF SECTION