DIVISION 30 10 03

NW10 –Wireless Ethernet Transmission Module 
with PoE

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- Wireless Ethernet Transmission Module 
with PoE

1.02 SECTION INCLUDES

- NW10 Wireless Ethernet Transmission Module
with PoE

1.03 REFERENCES

- Federal Communication Commission (FCC)

1.04 MODULE DESCRIPTION

- Performance Requirements: Provide 1 (one) 10/100/1000TX RJ-45 port, 1 (one) 10/100TX RJ-45 port and 1 (one) 5GHz 802.11a/n radio.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of device specified.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment. Storage Temperature not to exceed -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 5% to 95% (non-condensing).

1.08 WARRANTY

- Standard Communication Networks Comprehensive Lifetime Warranty: ComNet warrants the product to be free of factory defects under manufacture’s Lifetime Warranty as submitted under article 1.05 (A).

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer: Communication Networks; 3 Corporate Drive; Danbury CT 06810 USA; Telephone: 203-796-5300; Fax 203-796-5303; Email: sales@comnet.net; Internet: www.comnet.net

- Substitutions: Not Permitted

- Both modules of the wireless transmission link shall be provided by the same manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: NW10

  - GENERAL SPECIFICATIONS

- The wireless Ethernet module shall be a ComNet NW10. The module shall support IEEE 802.3 protocol using the 802.11a/n standard. The module shall feature 1 (one) 10/100/1000TX RJ-45 port and 1 (one) 10/100TX RJ-45 port that support one port as an 802.3af/at PoE Powered Device and the other port as an 802.3at PoE Power Sourcing Equipment. The module shall support two antennas utilizing MIMO technology and a maximum throughput of 240Mbps. The modules shall be encased in an IP67 dust and water immersion housing. The module shall provide power, link, and signal strength status indicating LED’s for monitoring proper system operation. The module shall have a lifetime warranty to reduce system life cycle cost in an event of a module failure.

- The module shall be configurable for either Client, single point Access Point or multi-point Access Point operation.

- The module shall operate in the license-free 5GHz frequency band.

- All modules shall support 1 (one) 10/100/1000TX RJ-45 port and 1 (one) 10/100TX RJ-45 port.

- All modules shall support passive PoE and IEEE802.3af/at PoE PD.

- All modules shall support IEEE802.3at PoE PSE.

- The module shall provide either auto-selectable or user static selectable frequency modes of operation.

- The module shall provide up to +30dBm RF power output.

- The module shall have selectable channel bandwidth capacity – 5, 10, 20 or 40MHz.

- The module shall use 2x2 MIMO technology.

- The module shall provide a throughput rate of up to 240Mbps.

- The module shall provide antenna alignment, signal strength, and site survey tools.

- The module shall be available with 19dBi gain integral antenna

- The module shall use WPA2 – either AES or TKIP encryption.

- The module shall have an operating temperature of -40°C to +75°C.

- The module radiated emission shall be compliant with FCC Part 15 standards.

- The module shall be supplied in an IP67 compliant housing.

- All modules and system parameters shall be configurable via a Graphical User Interface (GUI).

- The following IEEE Networking Standards shall be supported:

IEEE 802.3 10Base-T Ethernet

IEEE 802.3u 100Base-TX Fast Ethernet

IEEE 802.3ab 1000Base-T Gigabit Ethernet

IEEE 802.3af Power over Ethernet

IEEE 802.3at Power over Ethernet

IEEE 802.3D Spanning Tree Protocol (STP)

IEEE802.1X Port-based Network Access Control

NTP Client

- Wireless Radio Performance:

FCC 			+36dBm

(with MAC-lock enabled)	+49dBm

RF Output	+30dBm Rated Transmitter

Operational Frequency	5180-5825MHz

Bandwidths			5, 10, 20, 40MHz

- Wireless Antenna Performance:

Standard Internal Antenna	Dual Polarized

Gain	19dBi

Azimuth	17˚ Hor/Ver

Elevation	17˚ Hor/Ver

- MANAGEMENT

Configuration: Web, HTTPS, TFTP/Web Update for firmware and configuration backup/restore, DHCP Client and Server, User configurable Watchdog and Auto-Reboot Mechanism, Reset to default, Multi-Level Configuration and Monitoring Login Accounts, User Configurable Long Range Parameters, Admin password, Port Speed/Duplex control, status, SNMP v3.

NTP: Network Time Protocol to synchronize time from Internet

802.1x: Port-based Network Access Control

Embedded Firewall

QoS support

System Log

2.04 ELECTRICAL INTERFACE SPECIFICATIONS

- Data Interface: Ethernet IEEE 802.3

- Physical connector: 2 x RJ-45

- Data Rate: up to 1000Mbps

- Data Inputs/Outputs: 2

- Operation Mode: Full & Half  Duplex

2.05 WIRELESS INTERFACE SPECIFICATIONS

- Wireless Interface: Ethernet IEEE 802.11a, IEEE802.11n

- Number of wireless radios: 1

- Physical connector: 2 × N-Type Connector when external antenna model selected.

2.06 ELECTRICAL SPECIFICATIONS

- Operating Voltage: 24VDC @ 175mA.
48VDC @ 87.5mA

- PoE Support: IEEE 802.3af/at PD compliant, IEEE 802.3at PSE compliant

- Power Consumption: 4.2W max

2.07 MECHANICAL SPECIFICATIONS

- 10.6 in (W) x 10.6 in (H) x 2.9 in (D)

27 cm (W) x 27 cm (H) x 7.5 cm (D)

- Shipping Weight: <4.4lb/2kg

2.08 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C.

- Storage Temp: -40˚ C to +85˚ C.

- Relative Humidity: 5% to 95% (non-condensing).

2.09 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Federal Communications Commission (FCC) Part 15 Compliant

PART 3 - EXECUTION

3.01 EXAMINATION

- All components shall be inspected to verify physical condition and inclusion of all materials.

- The unit shall be comprised of one wireless module, one passive PoE power injection module and one pole mounting brackets for use with up to a 3 inch pole.

3.02 PREPARATION

- The wireless module shall be mounted with the pole bracket or other hardware high enough above the ground in order to gain a clear line of sight with the other end of the link. No trees, walls, buildings, moving objects or other obstacle shall interfere with the Fresnel zone of the RF signal.

3.03 INSTALLATION

- General: Locate wireless modules as indicated on the approved detail drawings and install module in compliance with the ComNet installation and operations manual.

3.04 TESTING

- Testing the Wireless Ethernet Link.

- Verify that the data cables are properly connected.

- Make sure that power is applied to all modules, controllers, and receiver drivers or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| NW10 SERIES | DESCRIPTION |
| --- | --- |
| NW10 | NetWave™ Wireless Ethernet High Throughput Unit (User Configurable Access Point or Client), 802.11a/n, One Integrated 19dBi 17° Beamwidth Antenna, Two 1Gb Ethernet Ports (Port 1 Supports 802.3af/at PD PoE, Port 2 Provides 802.3at PSE PoE), FCC Certified (US), Includes 24V Power Supply, Passive Injector & Pole Mounting Hardware Kit, Industrial Grade -40⁰C to +75⁰C, IP67 |

Table B: Product Accessory Chart

| ACCESSORIES | DESCRIPTION |
| --- | --- |
| NWBKT | NetWave™ Articulating Wall or Pole Mounting Bracket For Industrial NW1, NW2, NW10, NW8 Models, Supports Up To 3in/76mm Diameter Poles |

## END OF NW10 SECTION

DIVISION 30 10 02

NW10E –Wireless Ethernet Transmission Module 
with PoE

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- Wireless Ethernet Transmission Module 
with PoE

1.02 SECTION INCLUDES

- NW10E Wireless Ethernet Transmission Module
with PoE

1.03 REFERENCES

- European Union Compliance (CE)

1.04 MODULE DESCRIPTION

- Performance Requirements: Provide 2 (two) 10/100/1000TX RJ-45 ports and 1 (one) 5GHz 802.11a/n radio.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of device specified.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment. Storage Temperature not to exceed -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 5% to 95% (non-condensing).

1.08 WARRANTY

- Standard Communication Networks Comprehensive Lifetime Warranty: ComNet warrants the product to be free of factory defects under manufacture’s Lifetime Warranty as submitted under article 1.05 (A).

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer: Communication Networks; 3 Corporate Drive; Danbury CT 06810 USA; Telephone: 203-796-5300; Fax 203-796-5303; Email: sales@comnet.net; Internet: www.comnet.net

- Substitutions: Not Permitted

- Both modules of the wireless transmission link shall be provided by the same manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: NW10E

  - GENERAL SPECIFICATIONS

- The wireless Ethernet module shall be a ComNet NW10E. The module shall support IEEE 802.3 protocol using the 802.11a/n standard. The module shall feature 2(two) 10/100/1000TX RJ-45 ports that support one port as an 802.3af/at PoE Powered Device and the other port as an 802.3at PoE Power Sourcing Equipment. The module shall support two antennas utilizing MIMO technology and a maximum throughput of 240Mbps. The modules shall be encased in an IP67 dust and water immersion housing. The module shall provide power, link, and signal strength status indicating LED’s for monitoring proper system operation. The module shall have a lifetime warranty to reduce system life cycle cost in an event of a module failure.

- The module shall be configurable for either Client, single point Access Point or multi-point Access Point operation.

- The module shall operate in the license-free band B 5GHz frequency band.

- The module shall operate in the controlled band C 5GHz frequency band

- All modules shall support two, 10/100/1000Mbps RJ45 ports.

- All modules shall support passive PoE and IEEE802.3af/at PoE PD.

- All modules shall support IEEE802.3at PoE PSE.

- The module shall provide either auto-selectable or user static selectable frequency modes of operation.

- The module shall support Dynamic Frequency Selection (DFS) and Transmit Power Control (TPC) operation.

- The module shall provide up to +26dBm RF power output.

- The module shall have selectable channel bandwidth capacity – 10, 20 or 20/40MHz.

- The module shall use 2x2 MIMO technology.

- The module shall provide a throughput rate of up to 240Mbps.

- The module shall provide antenna alignment, signal strength, and site survey tools.

- The module shall be available with 19dBi or 8dBi gain integral antenna

- The module shall support the connection of external antenna via 2 x N-Type connector where appropriate model is selected.

- The module shall use WPA2 – either AES or TKIP encryption.

- The module shall have an operating temperature of -40°C to +75°C.

- The module radiated emission shall be compliant with ETSI standards.

- The module shall be supplied in an IP67 compliant housing.

- All modules and system parameters shall be configurable via a Graphical User Interface (GUI).

- The following IEEE Networking Standards shall be supported:

IEEE 802.3 10Base-T Ethernet

IEEE 802.3u 100Base-TX Fast Ethernet

IEEE 802.3ab 1000Base-T Gigabit Ethernet

IEEE 802.3af Power over Ethernet

IEEE 802.3at Power over Ethernet

IEEE 802.3D Spanning Tree Protocol (STP)

IEEE 802.11h DFS & TPC

IEEE802.1X Port-based Network Access Control

NTP Client

- Wireless Radio Performance:

EIRP (ETSI Band B)		+30dBm

EIRP (UK Band C)		+36dBm

EIRP (Eire Band C)		+33dBm

RF Output	+26dBm Rated Transmitter

Operational Frequency	5500-5700MHz

5745-5805MHz

Bandwidths			10, 20, 40MHz

- Wireless Antenna Performance:

Standard Internal Antenna	Dual Polarized

Gain	19dBi

Azimuth	17˚ Hor/Ver

Elevation	17˚ Hor/Ver

Wide Angle Internal Antenna	Dual Polarized

Gain	8dBi

Azimuth	70˚ Hor/Ver

Elevation	30˚ Hor/Ver

- MANAGEMENT

Configuration: Web, HTTPS, TFTP/Web Update for firmware and configuration backup/restore, DHCP Client, User configurable Watchdog and Auto-Reboot Mechanism, Reset to default, Multi-Level Configuration and Monitoring Login Accounts, User Configurable Long Range Parameters, Admin password, Port Speed/Duplex control, status, SNMP v2c.

NTP: Network Time Protocol to synchronize time from Internet

802.1x: Port-based Network Access Control

DHCP Server

System Log

2.04 ELECTRICAL INTERFACE SPECIFICATIONS

- Data Interface: Ethernet IEEE 802.3

- Physical connector: 2 x RJ-45

- Data Rate: up to 1000Mbps

- Data Inputs/Outputs: 2

- Operation Mode: Full & Half  Duplex

2.05 WIRELESS INTERFACE SPECIFICATIONS

- Wireless Interface: Ethernet IEEE 802.11a, IEEE802.11n

- Number of wireless radios: 1

- Physical connector: 2 × N-Type Connector when external antenna model selected.

2.06 ELECTRICAL SPECIFICATIONS

- Operating Voltage: 24VDC @ 175mA.
48VDC @ 87.5mA

- PoE Support: IEEE 802.3af/at PD compliant, IEEE 802.3at PSE compliant

- Power Consumption: 4.2W max

2.07 MECHANICAL SPECIFICATIONS

- 10.0 in (W) x 10.0 in (H) x 3.4 in (D)

25.7 cm (W) x 25.7 cm (H) x 8.6 cm (D)

- Shipping Weight: <4.2lb/1.9kg

2.08 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C.

- Storage Temp: -40˚ C to +85˚ C.

- Relative Humidity: 5% to 95% (non-condensing).

2.09 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- ETSI Compliant

PART 3 - EXECUTION

3.01 EXAMINATION

- All components shall be inspected to verify physical condition and inclusion of all materials.

- The unit shall be comprised of one wireless module, one passive PoE power injection module and one pole mounting brackets for use with up to a 3 inch pole.

3.02 PREPARATION

- The wireless module shall be mounted with the pole bracket or other hardware high enough above the ground in order to gain a clear line of sight with the other end of the link. No trees, walls, buildings, moving objects or other obstacle shall interfere with the Fresnel zone of the RF signal.

3.03 INSTALLATION

- General: Locate wireless modules as indicated on the approved detail drawings and install module in compliance with the ComNet installation and operations manual.

3.04 TESTING

- Testing the Wireless Ethernet Link.

- Verify that the data cables are properly connected.

- Make sure that power is applied to all modules, controllers, and receiver drivers or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| NW10E SERIES | DESCRIPTION |
| --- | --- |
| NW10E | NetWave™ Wireless Ethernet High Throughput Unit (User Configurable Access Point or Client), 802.11a/n, One Integrated 19dBi 17° Beamwidth Antenna, Two 1Gb Ethernet Ports (Port 1 Supports 802.3af/at PD PoE, Port 2 Provides 802.3at PSE PoE), ETSI Certified (EU), Includes 24V Power Supply, Passive Injector & Pole Mounting Hardware Kit, Industrial Grade -40⁰C to +75⁰C, IP67 |
| NW10E/IA870 | NetWave™ Wireless Ethernet High Throughput Unit (User Configurable Access Point or Client), 802.11a/n, One Integrated 8dBi 70° Beamwidth Antenna, Two 1Gb Ethernet Ports (Port 1 Supports 802.3af/at PD PoE, Port 2 Provides 802.3at PSE PoE), ETSI Certified (EU), Includes 24V Power Supply, Passive Injector & Pole Mounting Hardware Kit, Industrial Grade -40⁰C to +75⁰C, IP67 |
| NW10E/EXA | NetWave™ Wireless Ethernet High Throughput Unit (User Configurable Access Point or Client), 802.11a/n, One External Antenna (Sold Seperately), Two 1Gb Ethernet Ports (Port 1 Supports 802.3af/at PD PoE, Port 2 Provides 802.3at PSE PoE), ETSI Certified (EU), Includes 24V Power Supply, Passive Injector & Pole Mounting Hardware Kit, Industrial Grade -40⁰C to +75⁰C, IP67 |

Table B: Product Accessory Chart

| ACCESSORIES | DESCRIPTION |
| --- | --- |
| NWAVBSA1 | NetWave™ External Dual Polarization 18/17/16dBi Variable Beam Sector Antenna, User Configurable 60°, 90° or 120°, Two 3ft (1.2M) Long N-Type Outdoor Cables & Pole Mounting Hardware Included, IP65 |
| NWAODA1 | NetWave™ External Omni Directional Dual Band (2dBi@2.4GHz / 5dBi@5GHz) Antenna, 45° & 90° Articulating Joint, N-Type Connector, Each |
| NWBKT | NetWave™ Articulating Wall or Pole Mounting Bracket For Industrial NW1, NW2, NW10, NW8 Models, Supports Up To 3in/76mm Diameter Poles |

## END OF NW10E SECTION