DIVISION 28 05 33

CL(L,R)FE(X)POE(C,U) SERIES –FAST ETHERNET WITH PASS-THROUGH PoE and DIRECT INJECTION OVER COAX and UTP TRANSCEIVER

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- Ethernet Transceiver

1.02 SECTION INCLUDES

- CL(L,R)FE(X)POE(C,U) Series Fast Ethernet Transceiver

1.03 REFERENCES

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide an Ethernet transceiver system that transmits bi-directional 10 or 100 Mbps data with Pass-Through PoE and Direct Injection over 75-ohm coaxial cable or unshielded twisted pair (UTP).

1.05 SUBMITTALS

- Product Data: Manufacturer’s printed product data sheet for each type of Transceiver specified.

- Detail Drawings: Electrical connect drawings. Product mounting template.

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of Transceiver specified.

- Warranty: Manufacturer’s Printed Warranty

1.06 DELIVERY, STORAGE AND HANDLING

- Deliver materials in unopened factory packaging with Manufacturer’s bar coding to the job site.

- Inspect product upon delivery to assure that specified products have been received.

- Store in original packaging in a climate controlled environment. Storage Temperature not to exceed: -40˚ C to +80˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of -40˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing). If product is installed in condensation conditions, unit shall have conformal coating applied to the printed circuit board.

1.08 WARRANTY

- Standard Communication Networks Comprehensive Lifetime Warranty: ComNet warrants the product to be free of factory defects under manufacture’s Lifetime Warranty as submitted under article 1.05 (E)

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer: Communication Networks 3 Corporate Drive Danbury, CT 06810 USA; Telephone: 203-796-5300; Fax 203-796-5303; Email: sales@ComNet.net; Internet: www.ComNet.net

- Substitutions: Not Permitted

- All modules shall be supplied from a single manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

2.03 GENERAL SPECIFICATIONS

- The Fast Ethernet data transceiver system shall consist of a ComNet CL(L,R)FE(X)POE(C,U) series device.  The system shall consist of twelve models that support 10 or 100Mbps Ethernet as well as Pass-through Power over Ethernet (PoE) and Direct Injection over standard 75Ω coaxial cable or unshielded twisted pair (UTP). These models shall support transmission distances of up to 5,000 feet (1524m) at 10 Mbps, or 2,000 feet (548m) at 100 Mbps. The system shall transport one, four, eight, or sixteen channels. The IEEE 802.3-compliant extenders also meet the requirements for IEEE 802.3af/at PoE power, passing power to the powered device (PD). Direct Injection of 48 to 56 VDC into either a Local or Remote unit shall allow greater distances for PoE over standard 75Ω coaxial cable or unshielded twisted pair (UTP). The 1 CH units shall have the option of being powered by 12 VDC, 24 VAC, Pass-through PoE, or Direct Injection, whereas all Local units shall have the option of being powered by 12 VDC, Pass-through PoE or Direct Injection. LED indicators confirm operating status of the device. The devices shall be packaged in rugged aluminum housings and be designed for desktop or stand-alone mounting. The 8 channel and 16 channel systems shall be in a EIA 19” 1U high rack for easy installation. These modules shall be environmentally hardened to the requirements of NEMA TS-1/ TS-2. The module shall support the Ethernet data interface and be IEEE 802.3 compliant.  The unit is set to auto-negotiate data rates and can be used for half duplex or full duplex transmission.  The module shall require no in-field adjustments or in-line attenuators to ease installation.  The module shall provide power and link status indicating LED’s for monitoring proper system operation. The modules shall provide automatic re-settable solid-state current limiters and independent voltage regulators on each module to reduce the chance of a single point failure of the system. The module shall have an MTBF of >100,000 hours and operate in an environment of -40˚ C to +75˚ C and relative humidity between 0% to 95% (non-condensing). The module shall be UL and ULC listed and CE marked. The circuit board shall be UL 94 flame rated and meet all PCI standards.  All PC boards shall be designated with part number, PC board number and show appropriate revision number. Housing shall be of all metal construction.  All LED indicators and both electrical and mechanical connections shall be identified with silk-screened labels. The module shall have a Lifetime warranty to reduce system life cycle cost in an event of a module failure.

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE802.3

- Data Rate: 10/100 Mbps

- Operation Mode: Full or Half Duplex

2.05 STATUS INDICATORS

- Operating Power

- Ethernet: Traffic

- Link Extended Ethernet Traffic

2.06 CONNECTORS

- Coaxial: BNC, UTP: RJ45

- Power: Screw Clamp Terminal Strip.

- Data: RJ-45

2.07 ELECTRICAL SPECIFICATIONS

- Pass-through Mode:

- 1 Channel: 9-36 VDC, 24 VAC, PoE af, 1.5W

- 4 Channel: 12-15 VDC, 6W

- 8 Channel: 12-15 VDC, 12W

- 16 Channel: 12-15 VDC, 24W

- Direct Injection Mode:

- 1 Channel: 48-56 VDC, 30W

- 4 Channel: 48-56 VDC, 120W

- 8 Channel: 48-56 VDC, 240W & 12 to 15 VDC, 12 W

- 16 Channel: 48-56 VDC, 480W & 12 to 15 VDC, 24 W

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

- Circuit Board: UL 94 flame rated and meets all IPC standards.

2.08 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions: CL(L,R)FE1POE(C,U):

3.3 x 2.5 x 1.1 in, (8.4 x 6.4 x 2.8 cm)

Weight: 0.28lb (0.12kg)

- Surface Mount Dimensions: CL(L,R)FE4POE(C,U):

6.1 x 5.3 x 1.1 in, (15.5 x 13.5 x 2.8 cm)

Weight: <2 lbs. (0.9kg)

- Rack Mount Dimensions: CL(L,R)FE8POE(C,U):

6.1 x 19 x 1.75 in, (15.5 x 48.26 x 4.45 cm)

Weight: <5 lbs (2.3kg)

- Rack Mount Dimensions: CL(L,R)FE16POE(C,U):

6.1 x 19 x 1.75 in, (15.5 x 48.26 x 4.45 cm)

Weight: <5 lbs (2.3kg)

- Finish: Module shall be constructed of a metal enclosure with all connections and indicators silk-screened directly on unit.

2.9 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: -40˚ C to +75˚ C

- Storage Temp: -40˚ C to +80˚ C

- Relative Humidity: 0% to 95% (non-condensing). If product is installed under condensation conditions, unit shall have conformal coating applied to the printed circuit board. (Add –C to model number for conformal coated printed circuit board)

2.10 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- UL 94-flame rated PCB board

- European Listed (CE)

PART 3 - EXECUTION

3.01 EXAMINATION

- Inspect modules before installation.

- Modules shall be free of any cosmetic defects or damage.

- Shipping box shall include the module, power supply and operations manual.

3.02 PREPARATION

- Standalone Module (Surface Mount)

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet mounting template and installation manual.

- Rack Mount Module (19” Rack)

- Ensure the card cage is installed in a standard EIA 19” (482.6 mm) rack or wall standoff bracket adequate for the size and weight of the card cage. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet installation manual.

3.03 INSTALLATION

- General: Locate modules as indicated on the approved detail drawings and install module in compliance with the ComNet installation and operations manual.

3.04 TESTING

- Testing the Ethernet Link.

- Verify that the data leads and signal leads are properly connected.

- Make sure that power is applied to all modules, controllers, and receiver drivers or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

3.05 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| CL(L,R)FE(X)POE(C,U) SERIES | DESCRIPTION |
| --- | --- |
| CLLFE1POEC CLRFE1POEU CLLFE1POEU CLRFE1POEC CLLFE4POEC CLRFE4POEU CLLFE4POEU CLRFE4POEC CLLFE8POEC CLLFE8POEU CLLFE16POEC CLLFE16POEU | 1 Port Coax Ethernet Extender 1 Port UTP Ethernet Extender 1 Port UTP Ethernet Extender 1 Port Coax Ethernet Extender 4 Port Coax Ethernet Extender 4 Port UTP Ethernet Extender 4 Port UTP Ethernet Extender 4 Port Coax Ethernet Extender 8 Port Coax Ethernet Extender 8 Port UTP Ethernet Extender 16 Port Coax Ethernet Extender 16 Port UTP Ethernet Extender |

## END OF SECTION