DIVISION 30 10 02

NWK1 –Wireless Ethernet Transmission Kit 
with PoE

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- Wireless Ethernet Transmission Kit 
with PoE

1.02 SECTION INCLUDES

- NWK1 Wireless Ethernet Transmission Kit 
with PoE

1.03 REFERENCES

- Federal Communications Commission (FCC)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide 1 (one) 10/100TX RJ-45 port and 1 (one) 5GHz 802.11a/n radio.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of device specified.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment. Storage Temperature not to exceed -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 5% to 95% (non-condensing).

1.08 WARRANTY

- Standard Communication Networks Comprehensive Lifetime Warranty: ComNet warrants the product to be free of factory defects under manufacture’s Lifetime Warranty as submitted under article 1.05 (A).

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer: Communication Networks; 3 Corporate Drive; Danbury CT 06810 USA; Telephone: 203-796-5300; Fax 203-796-5303; Email: sales@comnet.net; Internet: www.comnet.net

- Substitutions: Not Permitted

- Both modules of the wireless transmission link shall be provided by the same manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: NWK1

  - GENERAL SPECIFICATIONS

- The wireless Ethernet system shall be a ComNet NWK1. The module shall support IEEE 802.3 protocol using the 802.11a/n standard. The module shall feature 1(one) 10/100TX RJ-45 port that supports 802.3af PoE as a Powered Device. The module shall support two antennas utilizing MIMO technology and a maximum throughput of 95Mbps. The wireless link shall be able to transmit an Ethernet signal 2 miles (3.2 km). The modules shall be encased in an IP67 dust and water immersion housing. The module shall provide power, link, and signal strength status indicating LED’s for monitoring proper system operation. The paired link shall be pre-configured by the manufacturer through MAC-locking the Client and Access Point modules. The module shall have a lifetime warranty to reduce system life cycle cost in an event of a module failure.

- The system shall provide point to point wireless connectivity.

- The system shall operate in the license-free 5GHz frequency band.

- All modules shall support one, 10/100Mbps RJ45 port.

- All modules shall support passive PoE and IEEE802.3af PoE PD.

- The system shall provide either auto-selectable or user static selectable frequency modes of operation.

- The system shall provide up to +26dBm RF power output.

- The system shall have selectable channel bandwidth capacity – 10, 20 or 20/40MHz.

- The system shall use 2x2 MIMO technology.

- The system shall provide a throughput rate of up to 95Mbps.

- The system shall provide antenna alignment, signal strength, and site survey tools.

- The system shall use WPA2 – either AES or TKIP encryption.

- The system shall have an operating temperature of -40°C to +75°C.

- The system radiated emission shall be compliant with FCC Part 15 standards.

- The system shall be supplied in an IP67 compliant housing.

- All modules and system parameters shall be configurable via a Graphical User Interface (GUI).

- The following IEEE Networking Standards shall be supported:

IEEE 802.3 10Base-T Ethernet

IEEE 802.3u 100Base-TX Fast Ethernet

IEEE 802.3af Power over Ethernet

IEEE 802.3D Spanning Tree Protocol (STP)

IEEE802.1X Port-based Network Access Control

NTP Client

- Wireless Radio Performance:

- FCC EIRP (with MAC-lock)	+45dBm

RF Output	+26dBm Rated Transmitter

Operational Frequency	5745-5825MHz

Bandwidths			10, 20, 40MHz

- Wireless Antenna Performance:

Standard Internal Antenna	Internal 19dBi Dual Polarized

Gain	19dBi

Azimuth	17˚ Hor/Ver

Elevation	17˚ Hor/Ver

- MANAGEMENT

Configuration: Web, HTTPS, TFTP/Web Update for firmware and configuration backup/restore, DHCP Client, User configurable Watchdog and Auto-Reboot Mechanism, Reset to default, Multi-Level Configuration and Monitoring Login Accounts, User Configurable Long Range Parameters, Admin password, Port Speed/Duplex control, status, SNMP v2c.

NTP: Network Time Protocol to synchronize time from Internet

802.1x: Port-based Network Access Control

DHCP Server

System Log

2.04 ELECTRICAL INTERFACE SPECIFICATIONS

- Data Interface: Ethernet IEEE 802.3

- Physical connector: RJ-45

- Data Rate: up to 95 Mbps

- Data Inputs/Outputs: 1

- Operation Mode: Half or Full Duplex

2.05 WIRELESS INTERFACE SPECIFICATIONS

- Wireless Interface: Ethernet IEEE 802.11a, IEEE802.11n

- Number of wireless radios: 1

- Physical connector: None

2.06 ELECTRICAL SPECIFICATIONS

- Operating Voltage: 24VDC @ 140mA.
48VDC @ 70mA

- PoE Support: IEEE 802.3af PD compliant

- Power Consumption: 3.5W max per module

2.07 MECHANICAL SPECIFICATIONS

- 10.0 in (W) x 10.0 in (H) x 3.4 in (D)

25.7 cm (W) x 25.7 cm (H) x 8.6 cm (D)

- Shipping Weight: <8.4lb/3.4kg

2.08 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C.

- Storage Temp: -40˚ C to +85˚ C.

- Relative Humidity: 5% to 95% (non-condensing).

2.09 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Federal Communications Commission (FCC) Part 15 Compliant

PART 3 - EXECUTION

3.01 EXAMINATION

- All components shall be inspected to verify physical condition and inclusion of all materials.

- The system shall be comprised of one Access Point module, one Client module, two passive PoE power injection modules and two pole mounting brackets for use with up to a 3 inch pole.

3.02 PREPARATION

- The Client and Access Point modules shall be mounted with the pole bracket or other hardware high enough above the ground in order to gain a clear line of sight between the two modules. No trees, walls, buildings, moving objects or other obstacle shall interfere with the Fresnel zone of the RF signal.

3.03 INSTALLATION

- General: Locate wireless modules as indicated on the approved detail drawings and install module in compliance with the ComNet installation and operations manual.

3.04 TESTING

- Testing the Wireless Ethernet Link.

- Verify that the data cables are properly connected.

- Make sure that power is applied to all modules, controllers, and receiver drivers or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| NWK1 SERIES | DESCRIPTION |
| --- | --- |
| NWK1 | NetWave™ Wireless Ethernet Pre-Configured Kit (Access Point & Client), 802.11a/n, One Integrated 19dBi 17° Beamwidth Antenna, One 100Mb Ethernet Port (Supports 802.3af PD PoE), FCC Certified (US), Includes 24V Power Supplies, Passive Injectors & Pole Mounting Hardware Kits, Industrial Grade -40⁰C to +75⁰C, IP67 |

Table B: Product Accessory Chart

| ACCESSORIES | DESCRIPTION |
| --- | --- |
| NWBKT | NetWave™ Articulating Wall or Pole Mounting Bracket For Industrial NW1, NW2, NW7, NW8 Models, Supports Up To 3in/76mm Diameter Poles |

## END OF NWK1 SECTION

DIVISION 30 10 02

NWK2 –Wireless Ethernet Transmission Kit 
with PoE

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- Wireless Ethernet Transmission Kit 
with PoE

1.02 SECTION INCLUDES

- NWK2 Wireless Ethernet Transmission Kit 
with PoE

1.03 REFERENCES

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide 1 (one) 10/100TX RJ-45 port and 1 (one) 5GHz 802.11a/n radio.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of device specified.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment. Storage Temperature not to exceed -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 5% to 95% (non-condensing).

1.08 WARRANTY

- Standard Communication Networks Comprehensive Lifetime Warranty: ComNet warrants the product to be free of factory defects under manufacture’s Lifetime Warranty as submitted under article 1.05 (A).

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer: Communication Networks; 3 Corporate Drive; Danbury CT 06810 USA; Telephone: 203-796-5300; Fax 203-796-5303; Email: sales@comnet.net; Internet: www.comnet.net

- Substitutions: Not Permitted

- Both modules of the wireless transmission link shall be provided by the same manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: NWK2

  - GENERAL SPECIFICATIONS

- The wireless Ethernet system shall be a ComNet NWK2. The module shall support IEEE 802.3 protocol using the 802.11a/n standard. The module shall feature 1(one) 10/100TX RJ-45 port that supports 802.3af PoE as a Powered Device. The module shall support two antennas utilizing MIMO technology and a maximum throughput of 95Mbps. The wireless link shall be able to transmit an Ethernet signal 2 km. The modules shall be encased in an IP67 dust and water immersion housing. The module shall provide power, link, and signal strength status indicating LED’s for monitoring proper system operation. The paired link shall be pre-configured by the manufacturer through MAC-locking the Client and Access Point modules. The module shall have a lifetime warranty to reduce system life cycle cost in an event of a module failure.

- The system shall provide point to point wireless connectivity.

- The system shall operate in the license-free Band B 5GHz frequency band.

- The system shall operate in the controlled Band C 5Ghz frequency band.

- All modules shall support one, 10/100Mbps RJ45 port.

- All modules shall support passive PoE and IEEE802.3af PoE PD.

- The system shall provide either auto-selectable or user static selectable frequency modes of operation.

- The system shall support Dynamic Frequency Selection (DFS) and Transmit Power Control (TPC) operation.

- The system shall provide up to +26dBm RF power output.

- The system shall have selectable channel bandwidth capacity – 10, 20 or 20/40MHz.

- The system shall use 2x2 MIMO technology.

- The system shall provide a throughput rate of up to 95Mbps.

- The system shall provide antenna alignment, signal strength, and site survey tools.

- The system shall use WPA2 – either AES or TKIP encryption.

- The system shall have an operating temperature of -40°C to +75°C.

- The system radiated emission shall be compliant with ETSI standards.

- The system shall be supplied in an IP67 compliant housing.

- All modules and system parameters shall be configurable via a Graphical User Interface (GUI).

- The following IEEE Networking Standards shall be supported:

IEEE 802.3 10Base-T Ethernet

IEEE 802.3u 100Base-TX Fast Ethernet

IEEE 802.3af Power over Ethernet

IEEE 802.3D Spanning Tree Protocol (STP)

IEEE 802.11h DFS & TPC

IEEE802.1X Port-based Network Access Control

NTP Client

- Wireless Radio Performance:

- ETSI EIRP band B		+30dBm

- UK band C EIRP		+36dBm

- Eire band C EIRP		+33dBm

RF Output	+26dBm Rated Transmitter

Operational Frequency	5500-5700MHz

5745-5805MHz

Bandwidths			10, 20, 40MHz

- Wireless Antenna Performance:

Standard Internal Antenna	Internal 19dBi Dual Polarized

Gain	19dBi

Azimuth	17˚ Hor/Ver

Elevation	17˚ Hor/Ver

- MANAGEMENT

Configuration: Web, HTTPS, TFTP/Web Update for firmware and configuration backup/restore, DHCP Client, User configurable Watchdog and Auto-Reboot Mechanism, Reset to default, Multi-Level Configuration and Monitoring Login Accounts, User Configurable Long Range Parameters, Admin password, Port Speed/Duplex control, status, SNMP v2c.

NTP: Network Time Protocol to synchronize time from Internet

802.1x: Port-based Network Access Control

DHCP Server

System Log

2.04 ELECTRICAL INTERFACE SPECIFICATIONS

- Data Interface: Ethernet IEEE 802.3

- Physical connector: RJ-45

- Data Rate: up to 95 Mbps

- Data Inputs/Outputs: 1

- Operation Mode: Half or Full Duplex

2.05 WIRELESS INTERFACE SPECIFICATIONS

- Wireless Interface: Ethernet IEEE 802.11a, IEEE802.11n

- Number of wireless radios: 1

- Physical connector: None

2.06 ELECTRICAL SPECIFICATIONS

- Operating Voltage: 24VDC @ 140mA.
48VDC @ 70mA

- PoE Support: IEEE 802.3af PD compliant

- Power Consumption: 3.5W max per module

2.07 MECHANICAL SPECIFICATIONS

- 10.0 in (W) x 10.0 in (H) x 3.4 in (D)

25.7 cm (W) x 25.7 cm (H) x 8.6 cm (D)

- Shipping Weight: <8.4lb/3.4kg

2.08 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C.

- Storage Temp: -40˚ C to +85˚ C.

- Relative Humidity: 5% to 95% (non-condensing).

2.09 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- ETSI Compliant

PART 3 - EXECUTION

3.01 EXAMINATION

- All components shall be inspected to verify physical condition and inclusion of all materials.

- The system shall be comprised of one Access Point module, one Client module, two passive PoE power injection modules and two pole mounting brackets for use with up to a 3 inch pole.

3.02 PREPARATION

- The Client and Access Point modules shall be mounted with the pole bracket or other hardware high enough above the ground in order to gain a clear line of sight between the two modules. No trees, walls, buildings, moving objects or other obstacle shall interfere with the Fresnel zone of the RF signal.

3.03 INSTALLATION

- General: Locate wireless modules as indicated on the approved detail drawings and install module in compliance with the ComNet installation and operations manual.

3.04 TESTING

- Testing the Wireless Ethernet Link.

- Verify that the data cables are properly                                                           connected.

- Make sure that power is applied to all modules, controllers, and receiver drivers or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| NWK2 SERIES | DESCRIPTION |
| --- | --- |
| NWK2 | NetWave™ Wireless Ethernet Pre-Configured Kit (Access Point & Client), 802.11a/n, One Integrated 19dBi 17° Beamwidth Antenna, One 100Mb Ethernet Port (Supports 802.3af PD PoE), ETSI Certified (EU), Includes 24V Power Supplies, Passive Injectors & Pole Mounting Hardware Kits, Industrial Grade -40⁰C to +75⁰C, IP67 |

Table B: Product Accessory Chart

| ACCESSORIES | DESCRIPTION |
| --- | --- |
| NWBKT | NetWave™ Articulating Wall or Pole Mounting Bracket For Industrial NW1, NW2, NW7, NW8 Models, Supports Up To 3in/76mm Diameter Poles |

## END OF NWK2 SECTION