DIVISION 27 21 29

CNGE4US SERIES –FOUR PORT UNMANAGED GIGABIT ETHERNET SWITCH ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- Four Port Unmanaged Fast Ethernet Switch

1.02 SECTION INCLUDES

- CNGE4US four port unmanaged Gigabit Ethernet switch, standalone or rack mountable

1.03 REFERENCES

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide four Gigabit Ethernet Ethernet ports –four ports, 1000 Mbps SFP based or 10/100/1000 Mbps SFP based

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment. Storage Temperature not to exceed: -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing). If product is installed in condensation conditions, add –C to the part number.

1.08 WARRANTY

- Standard Communication Networks Comprehensive Lifetime Warranty: ComNet warrants the product to be free of factory defects under manufacture’s Lifetime Warranty as submitted under article 1.05

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer: Communication Networks, Inc.; 3 Corporate Drive, Danbury, CT 06810  USA; Telephone: 203-796-5300; Fax 203-796-5303; Email: sales@comnet.com; Internet: www.comnet.com

- Substitutions: Not Permitted

- All modules shall be supplied from a single manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

2.03 GENERAL SPECIFICATIONS

- The Ethernet data switch shall be a ComNet CNGE4US series module.  The module shall support the transmission of four channels of 1000Base FX via single-mode or multimode fiber or 10/100/1000 Mbps Ethernet.  The module shall require no in-field electrical or optical adjustments or in-line attenuators to ease installation.  The module shall provide power, link speed, simplex or duplex transmission, and fiber port status indicating LED’s for monitoring proper system operation.  The modules shall provide automatic re-settable solid-state current limiters and independent voltage regulators on each module to reduce the chance of a single point failure of the system. The module shall be hot swappable in a rack mount system to reduce complete system shut down during maintenance or repair.  The module shall have a lifetime warranty to reduce system life cycle cost in an event of a module failure.

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE802.3

- Data Rate: 1000 Mbps

- Data Inputs: 4

- Operation Mode: Simplex or Duplex

2.05 OPTICAL SPECIFICATIONS

- ComNet Model Number CNGE4US

- Optical Fiber: 50/125 µm, 62.5/125 µm, or singlemode

- Number of Fibers Required: 1 or 2 per port, SFP dependant

- Optical Wavelength: SFP-dependant

- Optical Power Budget: SFP dependant

- Maximum Distance: SFP dependant

2.06 STATUS INDICATORS

- Power: On/Green – Off/Off

- Link/Speed:  100Mbps/Green – 10 Mbps/Red -No Fiber Connection/Off

- Simplex/Duplex: Simplex/Off, Duplex/Green.

2.07 CONNECTORS

- Optical: LC or SC, SFP dependant

- Electrical: RJ-45

- Power:  Terminal Block with Screw Clamps.

2.08 ELECTRICAL SPECIFICATIONS

- Power: 12VDC @ 800 mA

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

- Circuit Board: UL 94 flame rated and meets all IPC standards.

- Rack mount Card: Shall be hot-swappable with ComNet Model Number C1 (EIA 19” card cage)

2.09 MECHANICAL SPECIFICATIONS

- Dimensions: 7.0” x 4.9” x 1.0” (17.80 cm x 12.5 cm x 2.5 cm)

- Number of Rack Slots: 1

- Weight: <2.0 lbs./0.9kg

2.10 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C

- Storage Temp: -40˚ C to +85˚ C

- Relative Humidity: 0% to 95% (non-condensing). If product is installed under condensation conditions, unit shall have conformal coating applied to the printed circuit board. (Add –C to model number for conformal coated printed circuit board)

2.11 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Underwriters Laboratory (UL) Listing

- Underwriters Laboratory Canada (ULC)

- UL 94-flame rated PCB board

2.12 ACCESSORIES

- Card Cage: C1 Model Number C1 (EIA 19” card cage) shall be available to house and power rack mount modules.

- Blank Panels: C1 Model Number C1-BP shall be available to cover unused rack slots.

PART 3 - EXECUTION

3.01 EXAMINATION

- All optical connectors shall be covered with dust caps and remain on the module until installing cable connectors to module.

3.02 PREPARATION

- Standalone Module (Surface Mount)

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet mounting template and installation manual.

- Rack Mount Module (19” Rack)

- Shall be installed in the ComNet Model Number C1 card cage. Ensure the card cage is installed in a standard EIA 19” (482.6 mm) rack or wall standoff bracket adequate for the size and weight of the card cage. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet installation manual.

- Optical Fibers

- Caution: NEVER look into the end of an active optical fiber when using laser light output. Eye damage can occur. Wear eye protection when cleaving, terminating, and splicing fiber.

- The number and type (multimode or single-mode) of optical fiber shall meet the requirements of the ComNet model number in article 2.05 used in the installation.

- All optical fiber cables shall be properly installed and terminated with the mating optical connectors as submitted in article 2.07 (A).

- The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3dB of optical safety margin does not exceed the optical power budget as submitted in article 2.05.

- All optical connectors on cable shall be cleaned in compliance to optical connector manufactures specifications and covered with dust caps until connection to the fiber optic module.

3.03 INSTALLATION

- General: Locate fiber optic modules as indicated on the approved detail drawings and install module in compliance with the ComNet installation and operations manual.

3.04 TESTING

- Testing the Fiber Optic Ethernet Link.

- Verify that the data leads and optical fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, controllers, and receiver drivers or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

3.05 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all fiber scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| CNGE4US SERIES | DESCRIPTION |
| --- | --- |
| CNGE4US | 4-port unmanaged Gigabit Ethernet switch |

Table B: Product Compatibility Chart

| TRANSCEIVER | COMPATIBLE REPEATER / TRANSCEIVER |
| --- | --- |
| CNGE4US | CNGE4US, CNGE8US |
|  | CNGE3FE7MS2, CNGE2FE24MS, CNGE2FE24MS-PoE |

## END OF SECTION