DIVISION 27 21 29

CNFE5SMSPOE SERIES –FIVE PORT UNMANAGED FAST ETHERNET SWITCH ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- Five Port Unmanaged Fast Ethernet Switch

1.02 SECTION INCLUDES

- CNFE5SMSPOE is a five-port unmanaged fast Ethernet switch, standalone or rack mountable

- Din Rail mountable with optional accessories DINBKT1 or DINBKT4

1.03 REFERENCES

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide Five Fast Ethernet ports – 4 10/100 ports with POE (30W) and One port, 100 Mbps with uplink management functionality

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate-controlled environment. Storage Temperature not to exceed: -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing). If product is installed in condensation conditions, add –C to the part number.

1.08 WARRANTY

- Standard Communication Networks Comprehensive Lifetime Warranty: ComNet warrants the product to be free of factory defects under manufacture’s Lifetime Warranty as submitted under article 1.05

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer: Communication Networks, Inc.; 3 Corporate Drive, Danbury, CT 06810  USA; Telephone: 203-796-5300; Fax 203-796-5303; Email: sales@ComNet.com; Internet: www.ComNet.com

- Substitutions: Not Permitted

- All modules shall be supplied from a single manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

2.03 GENERAL SPECIFICATIONS

- The Ethernet data switch shall be a ComNet CNFE5SMSPOE series module.  The module shall support the transmission of four channels of 10 or 100 Mbps with 30 watts PoE over unshielded twisted pair and one channels of 10 or 100 Mbps Uplink over unshielded twisted pair. The module shall support the Ethernet data IEEE 802.3 protocol using Auto-negotiating and Auto-MDI/MDI-X features.  The module shall feature 5 electrical ports.  The module shall come with pre-programmed Port Based VLAN. The module shall provide power, link/data activity and PoE indicating LED’s for monitoring proper system operation. The module shall be hot swappable in a rack mount system to reduce complete system shut down during maintenance or repair.  The module shall have a lifetime warranty to reduce system life cycle cost in an event of a module failure.

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE802.3

- Data Rate: 10/100 Mbps

- Data Inputs: 5

- Operation Mode: Simplex or Duplex

2.05 STATUS INDICATORS

- Electrical Link/Data Activity

- Power

- PoE

2.06 CONNECTORS

- Power:  Terminal Block with Screw Clamps.

- Data: RJ-45

2.08 ELECTRICAL SPECIFICATIONS

- Power: 48VDC@2.6A with PoE,

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

- Circuit Board: UL 94 flame rated and meets all IPC standards.

- Rack mount Card: Shall be hot-swappable with ComNet Model Number C1 (EIA 19” card cage)

2.09 MECHANICAL SPECIFICATIONS

- Dimensions: 6.1 × 5.3 × 1.1 in. (15.5 × 13.5 × 2.8 cm).

- Number of Rack Slots: 1

- Weight: <2.0 lbs./0.9kg

2.10 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C

- Storage Temp: -40˚ C to +85˚ C

- Relative Humidity: 0% to 95% (non-condensing). If product is installed under condensation conditions, unit shall have conformal coating applied to the printed circuit board. (Add –C to model number for conformal coated printed circuit board)

2.11 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Underwriters Laboratory (UL) Listing

- Underwriters Laboratory Canada (ULC)

- UL 94-flame rated PCB board

2.12 ACCESSORIES

- Card Cage: C1 Model Number C1 (EIA 19” card cage) shall be available to house modules.

- Blank Panels: C1 Model Number C1-BP shall be available to cover unused rack slots.

- Din Rail Kit: DINBKT1 or DINBKT4 for din rail adaption

PART 3 - EXECUTION

3.01 EXAMINATION

Unit shall be kept in original shipping material and proper grounding should be taken during handling of product to minimize accidental grounding fault.

3.02 PREPARATION

- Standalone Module (Surface Mount)

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet mounting template and installation manual.

- Rack Mount Module (19” Rack)

- Shall be installed in the ComNet Model Number C1 card cage. Ensure the card cage is installed in a standard EIA 19” (482.6 mm) rack or wall standoff bracket adequate for the size and weight of the card cage. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet installation manual.

3.03 INSTALLATION

- General: Locate category cable (5E or better) as indicated on the approved detail drawings and install module in compliance with the ComNet installation and operations manual.

3.04 TESTING

- Testing the Data Link.

- Verify that the data leads and connectors are properly connected.

- Make sure that power is applied to switch, controllers, and receiver drivers or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

3.05 CLEANING

- Follow all instructions for proper use of solvents used for cleaning.

- At completion of the installation, dispose of all cable scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| CNFE5SMSPOE SERIES | DESCRIPTION |
| --- | --- |
| CNFE5SMSPOE | 5-port unmanaged Fast Ethernet switch |

Table B: Product Compatibility Chart

| TRANSCEIVER | COMPATIBLE REPEATER / TRANSCEIVER |
| --- | --- |
| CNFE5SMSPOE | CNFE4FX2TX2US, CNFE4FX4US, CNFE4TX4US |
|  | CNFE6+2USPOE, CNFE8FX8US, CNFE8TX8US |
|  | CNFE2MC, CNFE2MC-M, CNFE22MC, CNFE100x |
|  | CNGE3FE7MS2, CNGE2FE24MS, CNGE2FE24MS-PoE and other switches that follow IEEE standards. |

End of Section