DIVISION 27 21 29

CNGE2+2SMS – FOUR PORT FIBER OPTIC GIGABIT ETHERNET LIGHT MANAGED SWITCH

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- Four Port Gigabit Ethernet Lite Managed Switch

1.02 SECTION INCLUDES

- CNGE2+2SMS Series Ethernet Light Managed Switch

1.03 REFERENCES

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- European Union Compliance (CE)

- NEMA TS2-1998

- CALTRANS

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide 2 (two) 10/100/1000TX RJ-45 ports with 802.3af (15.4W), 802.3at (30W) or 802.3bt (60W) on Poe Models, and 2 (two) 100/1000FX SFP ports.

- The system shall have SFP ports allowing for the use of SFP modules for flexibility in determining operating wavelength, range, number of fibers, type of receptacle, and type of fiber.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of device specified.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate-controlled environment. Storage Temperature not to exceed -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing). If product is installed in condensation conditions, add /C to the part number.

1.08 WARRANTY

- Standard Communication Networks Comprehensive Lifetime Warranty: ComNet warrants the product to be free of factory defects under manufacture’s Lifetime Warranty as submitted under article 1.05 (A).

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer: Communication Networks; 3 Corporate Drive; Danbury CT 06810 USA; Telephone: 203-796-5300; Fax 203-796-5303; Email: sales@comnet.net; Internet: www.comnet.net

- Substitutions: Not Permitted

- All fiber optic Ethernet light managed switches and SFP modules shall be supplied from a single manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

  - GENERAL SPECIFICATIONS

- The Ethernet light managed switch system shall be a ComNet CNGE2+2SMS.  The module shall support transmission utilizing Category 5E cable or better, multimode, or single-mode fiber.  The module shall support the Ethernet data IEEE 802.3 protocol using Auto-negotiating and Auto-MDI/MDI-X features.  The module shall feature 2 (two) 10/100/1000TX RJ-45 ports with 802.3af (15.4W), 802.3at (30W) or 802.3bt (60W) on Poe Models, and 2 (two) 100/1000FX SFP ports. The module shall require no in-field electrical or optical adjustments or in-line attenuators to ease installation.  The module shall provide power, status, link speed, and fiber port status indicating LED’s for monitoring proper system operation.  The modules shall provide automatic re-settable solid-state current limiters on each module to reduce the chance of a single point failure of the system.  The module shall have redundant power supply connections to minimize single point failure.  The module shall provide a USB serial connection for local management of the device.  The module shall provide physical DIP switches for user selection of RSTP, IGMP, Redundant SFP Mode and Multicast Mux Mode without the need for any module configuration via a PC.  The module shall provide individual DIP switches for each SFP port for user selection of speed (100Mb or 1Gb).  The module shall support a user selectable Redundant SFP mode by which the module can support dual redundant paths using SFP ports with switch over from primary SFP to secondary SFP in the event of a link failure happening within 1 (one) second. The module shall have a lifetime warranty to reduce system life cycle cost in the event of a module failure.

- The following IEEE Networking Standards shall be supported:

IEEE 802.3 for 10BASE-T Ethernet

IEEE 802.3u for 100BASE-TX & 100BASE-FX

IEEE 802.3ab for 1000BASE-T

IEEE 802.3z for 1000BASE-X

IEEE 802.3x for Flow Control and Back-Pressure

IEEE 802.1w for Rapid Spanning Tree Protocol (RSTP)

IEEE802.1AB for Link Layer Discovery Protocol (LLDP)

- Switching Performance

Switch Technology: Store and Forward Technology with 8 Gbps Switching Fabric.

Switching Latency: 7µs

Transfer Packet Size: 64 bytes to 10K bytes

MAC Table: 1K MAC

- MANAGEMENT

Configuration: Web, CLI, SNMP

Features: Bootloader for firmware update, DHCP Client, Warm reboot, reset to default, Admin password, Port Speed/Duplex control, Port enable/disable, Port status, Port statistics, SNMP v1, v2c, and Traps.

SNMP MIB: Private MIB

IGMP Snooping: IGMP Snooping V1/V2 for multicast filtering with up to 64 groups.

Link Layer Discovery Protocol (LLDP)

Static Multicast MAC Routing

Port Security: Assign authorized MAC addresses to specific ports

Port Guardian: Physical port lockout in the event of a cable disconnection. Notification of such event via SNMP and ability to reset the port by a network administrator using remote SNMP command or through local CLI interface.

Active Ping Check: Monitor a user stated IP address on a per port basis with SNMP trap and port shutdown capability in the event of failure.

NETWORK REDUNDANCY

Rapid Spanning Tree Protocol: IEEE802.1w (RSTP).

Compatible with Legacy STP and IEEE802.1w.

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE802.3

- Data Rate: up to 1000 Mbps

- Data Ports: up to 4

- Operation Mode: Half or Full Duplex for RJ45 Ports and Full Duplex for SFP Ports

2.05 OPTICAL SPECIFICATIONS

- ComNet Model Number CNGE2+2SMS

- Number of Optical ports: up to 2 SFP-based

- Number of Fibers Required: 1 or 2, SFP-dependent

- Optical Wavelength: 850, 1310, 1550 nm or others, SFP-dependent

- Optical Power Budget: SFP-dependent

- Maximum Distance: up to 120 km (70 mi) single-mode, SFP-dependent

2.06 STATUS INDICATORS

- Power1/2: Proper Power = Green

- Status: System Good = Green, Fault = Red

- RJ-45 Link/Data: Green, No Link/No Data: Off

- SFP Link/Data: Green, No Link/No Data: Off

2.07 CONNECTORS

- Optical: LC or SC, SFP-dependent

- Power:  Screw Clamp Terminal Strip.

- Data: RJ-45

- Console: USB Type B Mini serial communication.

2.08 ELECTRICAL SPECIFICATIONS

- Power: Dual redundant inputs 9VDC to 36VDC or 24VAC @ 6 Watts maximum Non-PoE version. POE version 48-56VDC

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

- Circuit Board: UL 94 flame rated and meets all IPC standards.

2.09 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions: 4.1” x 3.7” x 1.46” (104 mm x 94 mm x 37 mm)

- Finish: Module shall be constructed of a metal enclosure with a powder coat.

- Weight: <2 lb/0.9kg

2.10 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C

- Storage Temp: -40˚ C to +85˚ C

- Relative Humidity: 0% to 95% (non-condensing).

2.11 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Underwriters Laboratory (UL) Listing Number: I.T.E. 6D16

- Underwriters Laboratory Canada (ULC) Listing Number: I.T.E. 6D16

- UL 94-flame rated PCB board: 94VO

2.12 ACCESSORIES

- Wall mount bracket automatically included

- DIN Rail mount optional with ComNet part code DINBKT4

PART 3 - EXECUTION

3.01 EXAMINATION

- All optical connectors shall be covered with dust caps and remain on the module until installing cable connectors to module.

3.02 PREPARATION

- DIN Rail Mount Module

- Shall be mounted on a properly installed DIN Rail adequate for the size and weight of the module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet mounting template and installation manual.

- Wall Mount (Surface Mount) Module

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet mounting template and installation manual.

- Optical Fibers

- Caution: NEVER look into the end of an active optical fiber when using laser light output. Eye damage can occur. Wear eye protection when cleaving, terminating, and splicing fiber.

- The number and type of optical fiber shall meet the requirements of the ComNet model number in article 2.05 used in the installation.

- All optical fiber cables shall be properly installed and terminated with the mating optical connectors as submitted in article 2.07 (A).

- The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3dB of optical safety margin does not exceed the optical power budget as submitted in article 2.05.

- All optical connectors on cable shall be cleaned in compliance to optical connector manufactures specifications and covered with dust caps until connection to the fiber optic module.

3.03 INSTALLATION

- General: Locate fiber optic modules as indicated on the approved detail drawings and install module in compliance with the ComNet installation and operations manual.

3.04 TESTING

- Testing the Fiber Optic Ethernet Link.

- Verify that the data leads and optical fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, controllers, and receiver drivers or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

3.05 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all fiber scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| CNGE2+2SMS PORTS† | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| CNGE2+2SMS ports 1 and 2 (RJ45) | Electrical 10/100/1000TX | 320 ft (100 m) |
| CNGE2+2SMS ports 3 and 4 (SFP) | Any combination of Electrical 10/100/1000TX via 10/100/1000TX SFP module using Category 5E cable or better, and/or Optical 100/1000FX via SFP module using multimode or singlemode fiber | Electrical: 320 ft (100 m) Optical: SFP-dependent up to 70 mi (120 km) |

* Maximum range will be limited by optical loss of the fiber, connectors, and splices.

Table B: Product Compatibility Chart

| CNGE2+2SMS PORTS | COMPATIBLE DEVICES |
| --- | --- |
| CNGE2+2SMS ports 1 and 2 | Any device that meets IEEE 802.3 10/100/1000BASE-TX protocols |
| CNGE2+2SMS ports 3 and 4 (SFP electrical) | Any device that meets IEEE 802.3 10/100/1000BASE-TX protocols |
| CNGE2+2SMS ports 3 and 4 (SFP optical) | Any device that meets IEEE 802.3u/z 100/1000BASE-FX protocols |

## END OF SECTION

DIVISION 27 21 29

CNGE2+2SMSPOE – FOUR PORT FIBER OPTIC GIGABIT ETHERNET LIGHT MANAGED SWITCH WITH POE+

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- Four Port Gigabit Ethernet Lite Managed PoE+ Switch

1.02 SECTION INCLUDES

- CNGE2+2SMSPOE Series Ethernet Light Managed PoE+ Switch

1.03 REFERENCES

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- European Union Compliance (CE)

- NEMA TS2-1998

- CALTRANS

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide 2 (two) 10/100/1000TX RJ-45 PoE+ (30W) ports, and 2 (two) 100/1000FX SFP ports.

- The system shall have SFP ports allowing for the use of SFP modules for flexibility in determining operating wavelength, range, number of fibers, type of receptacle, and type of fiber.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of device specified.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment. Storage Temperature not to exceed -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing). If product is installed in condensation conditions, add /C to the part number.

1.08 WARRANTY

- Standard Communication Networks Comprehensive Lifetime Warranty: ComNet warrants the product to be free of factory defects under manufacture’s Lifetime Warranty as submitted under article 1.05 (A).

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer: Communication Networks; 3 Corporate Drive; Danbury CT 06810 USA; Telephone: 203-796-5300; Fax 203-796-5303; Email: sales@comnet.net; Internet: www.comnet.net

- Substitutions: Not Permitted

- All fiber optic Ethernet light managed switches and SFP modules shall be supplied from a single manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

  - GENERAL SPECIFICATIONS

- The Ethernet light managed switch system shall be a ComNet CNGE2+2SMSPOE.  The module shall support transmission utilizing Category 5 cable or better, multimode, or single-mode fiber.  The module shall support the Ethernet data IEEE 802.3 protocol using Auto-negotiating and Auto-MDI/MDI-X features.  The module shall feature 2 (two) 10/100/1000TX RJ-45 PoE+ ports (30W), and 2 (two) 100/1000FX SFP ports. The module shall require no in-field electrical or optical adjustments or in-line attenuators to ease installation.  The module shall provide power, status, link speed, PoE and fiber port status indicating LED’s for monitoring proper system operation.  The modules shall provide automatic re-settable solid-state current limiters on each module to reduce the chance of a single point failure of the system.  The module shall have redundant power supply connections to minimize single point failure.  The module shall provide a USB serial connection for local management of the device.  The module shall provide physical DIP switches for user selection of RSTP, IGMP, Redundant SFP Mode and Multicast Mux Mode without the need for any module configuration via a PC.  The module shall provide individual DIP switches for each SFP port for user selection of speed (100Mb or 1Gb).  The module shall support a user selectable Redundant SFP mode by which the module can support dual redundant paths using SFP ports with switch over from primary SFP to secondary SFP in the event of a link failure happening within 1 (one) second.  The module shall support 2 (two) independent contact inputs and 2 (two) independent relay outputs that can be controlled by web GUI and SNMP commands. The module shall have a lifetime warranty to reduce system life cycle cost in the event of a module failure.

- The following IEEE Networking Standards shall be supported:

IEEE 802.3 for 10BASE-T Ethernet

IEEE 802.3u for 100BASE-TX & 100BASE-FX

IEEE 802.3ab for 1000BASE-T

IEEE 802.3z for 1000BASE-X

IEEE 802.3x for Flow Control and Back-Pressure

IEEE 802.1w for Rapid Spanning Tree Protocol (RSTP)

IEEE802.1AB for Link Layer Discovery Protocol (LLDP)

IEEE802.3at for Power Over Ethernet (PoE+)

- Switching Performance

Switch Technology: Store and Forward Technology with 8 Gbps Switching Fabric.

Switching Latency: 7µs

Transfer Packet Size: 64 bytes to 10K bytes

MAC Table: 1K MAC

- MANAGEMENT

Configuration: Web, CLI, SNMP

Features: Bootloader for firmware update, DHCP Client, Warm reboot, Reset to default, Admin password, Port Speed/Duplex control, Port enable/disable, Port status, Port statistics, SNMP v1, v2c, and Traps.

SNMP MIB: Private MIB

IGMP Snooping: IGMP Snooping V1/V2 for multicast filtering with up to 64 groups.

Link Layer Discovery Protocol (LLDP)

Static Multicast MAC Routing

PoE Configuration and Status

Port Security: Assign authorized MAC addresses to specific ports

Port Guardian: Physical port lockout in the event of a cable disconnection. Notification of such event via SNMP and ability to reset the port by a network administrator using remote SNMP command or through local CLI interface or by triggering a local contact input.

Active Ping Check: Monitor a user stated IP address on a per port basis with SNMP trap, PoE reset, relay output trigger and port shutdown capability in the event of failure.

NETWORK REDUNDANCY

Rapid Spanning Tree Protocol: IEEE802.1w (RSTP).

Compatible with Legacy STP and IEEE802.1w.

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE802.3

- Data Rate: up to 1000 Mbps

- Data Ports: up to 4

- Operation Mode: Half or Full Duplex for RJ45 Ports and Full Duplex for SFP Ports

2.05 OPTICAL SPECIFICATIONS

- ComNet Model Number CNGE2+2SMSPOE

- Number of Optical ports: up to 2 SFP-based

- Number of Fibers Required: 1 or 2, SFP-dependent

- Optical Wavelength: 850, 1310, 1550 nm or others, SFP-dependent

- Optical Power Budget: SFP-dependent

- Maximum Distance: up to 120 km (70 mi) single-mode, SFP-dependent

2.06 STATUS INDICATORS

- Power1/2: Proper Power = Green

- Status: System Good = Green, Fault = Red

- RJ-45 Link/Data: Green,  No Link/No Data: Off

- SFP Link/Data: Green, No Link/No Data: Off

- PoE: PoE On = Green, No PoE = Off

2.07 CONNECTORS

- Optical: LC or SC, SFP-dependent

- Power:  Screw Clamp Terminal Strip.

- Data: RJ-45

- Console: USB Type B Mini serial communication.

2.08 ELECTRICAL SPECIFICATIONS

- Power: Dual redundant inputs 48VDC to 56VDC @ 66 Watts maximum (with full PoE load)

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

- Circuit Board: UL 94 flame rated and meets all IPC standards.

2.09 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions: 4.1” x 3.7” x 1.46” (104 mm x 94 mm x 37 mm)

- Finish: Module shall be constructed of a metal enclosure with a powder coat.

- Weight: <2 lb/0.9kg

2.10 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C

- Storage Temp: -40˚ C to +85˚ C

- Relative Humidity: 0% to 95% (non-condensing).

2.11 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Underwriters Laboratory (UL) Listing Number: I.T.E. 6D16

- Underwriters Laboratory Canada (ULC) Listing Number: I.T.E. 6D16

- UL 94-flame rated PCB board: 94VO

2.12 ACCESSORIES

- Wall mount bracket automatically included

- DIN Rail mount optional with ComNet part code DINBKT4

PART 3 - EXECUTION

3.01 EXAMINATION

- All optical connectors shall be covered with dust caps and remain on the module until installing cable connectors to module.

3.02 PREPARATION

- DIN Rail Mount Module

- Shall be mounted on a properly installed DIN Rail adequate for the size and weight of the module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet mounting template and installation manual.

- Wall Mount (Surface Mount) Module

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet mounting template and installation manual.

- Optical Fibers

- Caution: NEVER look into the end of an active optical fiber when using laser light output. Eye damage can occur. Wear eye protection when cleaving, terminating, and splicing fiber.

- The number and type of optical fiber shall meet the requirements of the ComNet model number in article 2.05 used in the installation.

- All optical fiber cables shall be properly installed and terminated with the mating optical connectors as submitted in article 2.07 (A).

- The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3dB of optical safety margin does not exceed the optical power budget as submitted in article 2.05.

- All optical connectors on cable shall be cleaned in compliance to optical connector manufactures specifications and covered with dust caps until connection to the fiber optic module.

3.03 INSTALLATION

- General: Locate fiber optic modules as indicated on the approved detail drawings and install module in compliance with the ComNet installation and operations manual.

3.04 TESTING

- Testing the Fiber Optic Ethernet Link.

- Verify that the data leads and optical fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, controllers, and receiver drivers or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

3.05 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all fiber scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| CNGE2+2SMSPOE PORTS† | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| CNGE2+2SMSPOE ports 1 and 2 (RJ45) | Electrical 10/100/1000TX | 320 ft (100 m) |
| CNGE2+2SMSPOE ports 3 and 4 (SFP) | Any combination of Electrical 10/100/1000TX via 10/100/1000TX SFP module using Category 5 cable or better, and/or Optical 100/1000FX via SFP module using multimode or singlemode fiber | Electrical: 320 ft (100 m) Optical: SFP-dependent up to 70 mi (120 km) |

* Maximum range will be limited by optical loss of the fiber, connectors, and splices.

Table B: Product Compatibility Chart

| CNGE2+2SMSPOE PORTS | COMPATIBLE DEVICES |
| --- | --- |
| CNGE2+2SMSPOE ports 1 and 2 | Any device that meets IEEE 802.3 10/100/1000BASE-TX protocols |
| CNGE2+2SMSPOE ports 3 and 4 (SFP electrical) | Any device that meets IEEE 802.3 10/100/1000BASE-TX protocols |
| CNGE2+2SMSPOE ports 3 and 4 (SFP optical) | Any device that meets IEEE 802.3u/z 100/1000BASE-FX protocols |

## END OF SECTION

DIVISION 27 21 29

CNGE2+2SMSPOEHO – FOUR PORT FIBER OPTIC GIGABIT ETHERNET LIGHT MANAGED SWITCH WITH POE++

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- Four Port Gigabit Ethernet Lite Managed PoE++ Switch

1.02 SECTION INCLUDES

- CNGE2+2SMSPOE Series Ethernet Light Managed PoE++ Switch

1.03 REFERENCES

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- European Union Compliance (CE)

- NEMA TS2-1998

- CALTRANS

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide 2 (two) 10/100/1000TX RJ-45 PoE++ (60W) ports, and 2 (two) 100/1000FX SFP ports.

- The system shall have SFP ports allowing for the use of SFP modules for flexibility in determining operating wavelength, range, number of fibers, type of receptacle, and type of fiber.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of device specified.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment. Storage Temperature not to exceed -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing). If product is installed in condensation conditions, add /C to the part number.

1.08 WARRANTY

- Standard Communication Networks Comprehensive Lifetime Warranty: ComNet warrants the product to be free of factory defects under manufacture’s Lifetime Warranty as submitted under article 1.05 (A).

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer: Communication Networks; 3 Corporate Drive; Danbury CT 06810 USA; Telephone: 203-796-5300; Fax 203-796-5303; Email: sales@comnet.net; Internet: www.comnet.net

- Substitutions: Not Permitted

- All fiber optic Ethernet light managed switches and SFP modules shall be supplied from a single manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

  - GENERAL SPECIFICATIONS

- The Ethernet light managed switch system shall be a ComNet CNGE2+2SMSPOEHO.  The module shall support transmission utilizing Category 5 cable or better, multimode, or single-mode fiber.  The module shall support the Ethernet data IEEE 802.3 protocol using Auto-negotiating and Auto-MDI/MDI-X features.  The module shall feature 2 (two) 10/100/1000TX RJ-45 PoE++ ports (60W), and 2 (two) 100/1000FX SFP ports. The module shall require no in-field electrical or optical adjustments or in-line attenuators to ease installation.  The module shall provide power, status, link speed, PoE and fiber port status indicating LED’s for monitoring proper system operation.  The modules shall provide automatic re-settable solid-state current limiters on each module to reduce the chance of a single point failure of the system.  The module shall have redundant power supply connections to minimize single point failure.  The module shall provide a USB serial connection for local management of the device.  The module shall provide physical DIP switches for user selection of RSTP, IGMP, Redundant SFP Mode and Multicast Mux Mode without the need for any module configuration via a PC.  The module shall provide individual DIP switches for each SFP port for user selection of speed (100Mb or 1Gb).  The module shall support a user selectable Redundant SFP mode by which the module can support dual redundant paths using SFP ports with switch over from primary SFP to secondary SFP in the event of a link failure happening within 1 (one) second.  The module shall support 2 (two) independent contact inputs and 2 (two) independent relay outputs that can be controlled by web GUI and SNMP commands. The module shall have a lifetime warranty to reduce system life cycle cost in the event of a module failure.

- The following IEEE Networking Standards shall be supported:

IEEE 802.3 for 10BASE-T Ethernet

IEEE 802.3u for 100BASE-TX & 100BASE-FX

IEEE 802.3ab for 1000BASE-T

IEEE 802.3z for 1000BASE-X

IEEE 802.3x for Flow Control and Back-Pressure

IEEE 802.1w for Rapid Spanning Tree Protocol (RSTP)

IEEE802.1AB for Link Layer Discovery Protocol (LLDP)

IEEE802.3at for Power Over Ethernet (PoE+)

- Switching Performance

Switch Technology: Store and Forward Technology with 8 Gbps Switching Fabric.

Switching Latency: 7µs

Transfer Packet Size: 64 bytes to 10K bytes

MAC Table: 1K MAC

- MANAGEMENT

Configuration: Web, CLI, SNMP

Features: Bootloader for firmware update, DHCP Client, Warm reboot, Reset to default, Admin password, Port Speed/Duplex control, Port enable/disable, Port status, Port statistics, SNMP v1, v2c, and Traps.

SNMP MIB: Private MIB

IGMP Snooping: IGMP Snooping V1/V2 for multicast filtering with up to 64 groups.

Link Layer Discovery Protocol (LLDP)

Static Multicast MAC Routing

PoE Configuration and Status

Port Security: Assign authorized MAC addresses to specific ports

Port Guardian: Physical port lockout in the event of a cable disconnection. Notification of such event via SNMP and ability to reset the port by a network administrator using remote SNMP command or through local CLI interface or by triggering a local contact input.

Active Ping Check: Monitor a user stated IP address on a per port basis with SNMP trap, PoE reset, relay output trigger and port shutdown capability in the event of failure.

NETWORK REDUNDANCY

Rapid Spanning Tree Protocol: IEEE802.1w (RSTP).

Compatible with Legacy STP and IEEE802.1w.

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE802.3

- Data Rate: up to 1000 Mbps

- Data Ports: up to 4

- Operation Mode: Half or Full Duplex for RJ45 Ports and Full Duplex for SFP Ports

2.05 OPTICAL SPECIFICATIONS

- ComNet Model Number CNGE2+2SMSPOEHO

- Number of Optical ports: up to 2 SFP-based

- Number of Fibers Required: 1 or 2, SFP-dependent

- Optical Wavelength: 850, 1310, 1550 nm or others, SFP-dependent

- Optical Power Budget: SFP-dependent

- Maximum Distance: up to 120 km (70 mi) single-mode, SFP-dependent

2.06 STATUS INDICATORS

- Power1/2: Proper Power = Green

- Status: System Good = Green, Fault = Red

- RJ-45 Link/Data: Green,  No Link/No Data: Off

- SFP Link/Data: Green, No Link/No Data: Off

- PoE: PoE On = Green, No PoE = Off

2.07 CONNECTORS

- Optical: LC or SC, SFP-dependent

- Power:  Screw Clamp Terminal Strip.

- Data: RJ-45

- Console: USB Type B Mini serial communication.

2.08 ELECTRICAL SPECIFICATIONS

- Power: Dual redundant inputs 48VDC to 56VDC @ 126 Watts maximum (with full PoE load)

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

- Circuit Board: UL 94 flame rated and meets all IPC standards.

2.09 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions: 4.1” x 3.7” x 1.46” (104 mm x 94 mm x 37 mm)

- Finish: Module shall be constructed of a metal enclosure with a powder coat.

- Weight: <2 lb/0.9kg

2.10 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C

- Storage Temp: -40˚ C to +85˚ C

- Relative Humidity: 0% to 95% (non-condensing).

2.11 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Underwriters Laboratory (UL) Listing Number: I.T.E. 6D16

- Underwriters Laboratory Canada (ULC) Listing Number: I.T.E. 6D16

- UL 94-flame rated PCB board: 94VO

2.12 ACCESSORIES

- Wall mount bracket automatically included

- DIN Rail mount optional with ComNet part code DINBKT4

PART 3 - EXECUTION

3.01 EXAMINATION

- All optical connectors shall be covered with dust caps and remain on the module until installing cable connectors to module.

3.02 PREPARATION

- DIN Rail Mount Module

- Shall be mounted on a properly installed DIN Rail adequate for the size and weight of the module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet mounting template and installation manual.

- Wall Mount (Surface Mount) Module

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the ComNet mounting template and installation manual.

- Optical Fibers

- Caution: NEVER look into the end of an active optical fiber when using laser light output. Eye damage can occur. Wear eye protection when cleaving, terminating, and splicing fiber.

- The number and type of optical fiber shall meet the requirements of the ComNet model number in article 2.05 used in the installation.

- All optical fiber cables shall be properly installed and terminated with the mating optical connectors as submitted in article 2.07 (A).

- The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3dB of optical safety margin does not exceed the optical power budget as submitted in article 2.05.

- All optical connectors on cable shall be cleaned in compliance to optical connector manufactures specifications and covered with dust caps until connection to the fiber optic module.

3.03 INSTALLATION

- General: Locate fiber optic modules as indicated on the approved detail drawings and install module in compliance with the ComNet installation and operations manual.

3.04 TESTING

- Testing the Fiber Optic Ethernet Link.

- Verify that the data leads and optical fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, controllers, and receiver drivers or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

3.05 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all fiber scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| CNGE2+2SMSPOEHO PORTS† | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| CNGE2+2SMSPOEHO ports 1 and 2 (RJ45) | Electrical 10/100/1000TX | 320 ft (100 m) |
| CNGE2+2SMSPOEHO ports 3 and 4 (SFP) | Any combination of Electrical 10/100/1000TX via 10/100/1000TX SFP module using Category 5 cable or better, and/or Optical 100/1000FX via SFP module using multimode or singlemode fiber | Electrical: 320 ft (100 m) Optical: SFP-dependent up to 70 mi (120 km) |

* Maximum range will be limited by optical loss of the fiber, connectors, and splices.

Table B: Product Compatibility Chart

| CNGE2+2SMSPOEHO PORTS | COMPATIBLE DEVICES |
| --- | --- |
| CNGE2+2SMSPOEHO ports 1 and 2 | Any device that meets IEEE 802.3 10/100/1000BASE-TX protocols |
| CNGE2+2SMSPOEHO ports 3 and 4 (SFP electrical) | Any device that meets IEEE 802.3 10/100/1000BASE-TX protocols |
| CNGE2+2SMSPOEHO ports 3 and 4 (SFP optical) | Any device that meets IEEE 802.3u/z 100/1000BASE-FX protocols |

## END OF SECTION