DIVISION 27 21 29

PS48VDC-10A

SWITCHING MODE POWER SUPPLY

ENGINEERING SPECIFICATIONS

PART 1 - GENERAL

- SUMMARY

  - Switching Mode Power Supply

- SECTION INCLUDES

  - PS48VDC-10A

- REFERENCES

  - Underwriters Laboratory (UL)

  - Underwriters Laboratory Canada (ULC)

  - European Union Compliance (CE)

  - Federal Communications Commission (FCC)

  - NEMA TS2-1998

  - CALTRANS

  - Technischer Uberwachungs-Verein (TÜV)

- SYSTEM DESCRIPTION

  - Performance Requirements: Provide a power supply to power Ethernet switches that utilize Power over Ethernet (PoE).

- SUBMITTALS

  - Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of device specified.

- DELIVERY, STORAGE AND HANDLING

  - Store in original packaging in a climate controlled environment.  Storage Temperature not to exceed -25˚ C to +85˚ C

- PROJECT/SITE CONDITIONS

  - Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –25˚ C to +71˚ C without the assistance of fan-forced cooling.

  - Humidity Requirements: Products shall operate in an environment with relative humidity of 20% to 95% (non-condensing).

PART 2 - PRODUCTS

- MANUFACTURER

  - Acceptable Manufacturer: Communication Networks; 3 Corporate Drive; Danbury CT 06810 USA; Telephone: 203-796-5300; Fax 203-796-5303; Email: sales@ComNet.net; Internet: www.ComNet.net

  - Substitutions: Not Permitted

- GENERAL SPECIFICATIONS

  - The power supply shall be a switching mode power supply (SMPS).

  - The SMPS shall take 90 to 264 VAC @ 47 to 63 Hz or 120 to 370 VDC as input voltage.

  - The SMPS shall produce a stable 48 to 53 VDC and be capable of supplying 5 amperes at 48 VDC (240 W).

  - Line regulation shall be within +/- 0.5%.

  - Ripple shall be no more than 150 mV, pk-pk.

  - The SMPS shall incorporate automatic power factor correction.

  - To minimize damage to a powered device (PD), the SMPS shall have output overvoltage protection to limit the maximum output voltage to 57 to 63 VDC.

  - The SMPS shall incorporate current limiters to provide output short circuit protection.

  - The SMPS shall be capable of being mounted to standard 7.5 or 15 mm DIN rail.

- STATUS INDICATORS

  - Power: Proper Power = Green

- CONNECTORS

  - Power Connections: Screw terminals (10 to 24 AWG wire)

- MECHANICAL SPECIFICATIONS;

Screw terminal connector: 12.5 × 17.5 × 12.3 cm (4.9 × 6.9 × 4.8 in)

Plug connector version: 14.2 × 17.5 × 12.3 cm (5.6 × 6.9 × 4.8 in)

  - Finish: Module shall be constructed of a metal enclosure with a powder coat.

  - Weight: <4.3 lb/1.9 kg

- ENVIRONMENTAL SPECIFICATIONS

  - Operating Temp: –25˚ C to +71˚ C

  - Storage Temp: -25˚ C to +85˚ C

  - Relative Humidity: 20% to 95% (non-condensing).

  - Cooling: Natural convection

- APPROVALS AND EMC COMPLIANCE

- Insulation voltage I/O 3.000Vac

- Insulation resistance I/O @ 500VDC 100Mohm

- UL / cUL UL508 listed, UL60950-1, Recognized

- TUV EN60950-1

- CE EN61000-6-3

- EN55022 class B

- EN61000-3-2

- EN61000-3-3

- EN61000-6-2

- EN55024

PART 3 - EXECUTION

- EXAMINATION

  - The SMPS exterior should be free from dents or other damage that would indicate a compromise in performance or safety.

  - The DIN rail clip should be in good condition and solidly connected to the switch.

  - Ventilation holes shall be in good condition and free from debris to allow natural convection to occur.

  - Screw terminals shall be in good condition.

- MOUNTING

  - The SMPS switch shall be mounted such that its chassis is at least 25 mm (1 in) on all sides from any other objects to allow adequate cooling to occur.